## Main
FPA-1000 BatteryCalc V2.01
Project Name: | [5 empty] | Standby Hours: |  | 24
Project ID: | [5 empty] | Alarm Mins: |  | 5 |  | Extra Circuit Capacity: |  |  | 10%
Prepared By: | [5 empty] | Global Wire Type: |  | #12 Solid |  | Voltage Drop: |  |  | 25%
| Date: | [8 empty] | Aux/NAC EOL Voltage(V): |  |  | 20
Panel ID: |  | Panel ID: |  |  |  |  | Model: | FPA-1000 |  | Max Circuit Cur.: |  |  | 2.5Amps
Location: |  | Location: |  |  |  |  | Volts: | 24 VDC |  | Max Panel Cur.: |  |  | 5 Amps
| Circuit Type |  |  | Current Draw @ 24 VDC |  | Line Current Draw |  | Wire AWG & Type | Ohms Per 1000 Ft. | Length(ft) Per Circuit | Actual Ohms | Volts @ EOL | %Drop | Open detect voltage (v) | Re-init Time (s)
|  |  |  | Standby | Alarm | Standby | Alarm
| SLC 1 Devices |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 | 3000 | 12.06 | 38 | 0% | 0 | 0
| SLC 2 Devices |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 | 3000 | 12.06 | 38 | 0% | 0 | 0
| Aux Power |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 | 3000 | 12.06 | 24 | 0% | 0.2043
| MB NAC 1 |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 | 3000 | 12.06 | 24 | 0% | 0.2043
| MB NAC 2 |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 |  | 0 | 24 | 0%
| Option Bus |  | 0 | 0 | 0 | 0 | 0 | #12 Solid | 2.01 | 0 | 0 | Max. Values For Bus
| SLC 2 Card |  | 0.06 | 0.06 | 0.06
| CITY TIE |  | 0 | 0 | 0
| NETWORK CARD |  | 0 | 0 | 0
FPA-1000 Panel (incl. SLC 1 Card) |  |  |  | 0.17 | 0.31
Total Standby Current (Amps) |  |  |  | 0.23 | 0.37 | Total Alarm Current (Amps)
Standby Time In Hours |  |  |  | 24 | 5 | Alarm Time In Min
Total Standby AH Required |  |  |  | 5.52 | 0.030833 | Total Alarm AH Required
Total Combined AH Required |  |  |  | 5.5508
Multiply by Battery Derating Factor |  |  |  | 10%
Minimum Battery AmpHours Required |  |  |  | 6.1059
Config
Config
Config
Config
Config
Config
Config
Config
Config
Warning thresholds
Project Varibles
Config
Config
Config
Config
Config
Config

## Data (hidden)
Conductor Properties NEC Chap. 9
Wire Type | Ohms Per 1000 ft.
#12 Solid | 2.01
#12 Stranded | 2.05
#14 Solid | 3.19
#14 Stranded | 3.26
#16 Solid | 5.08
#16 Stranded | 5.29
#18 Solid | 8.08
#18 Stranded | 8.45
Conductor Properties NEC Chap. 9
Wire Type | Ohms Per 1000 ft.
#12 Solid | 2.01
#14 Solid | 3.19
#16 Solid | 4.03
#18 Solid | 6.41
Unused |  |  |  | 18 | 16 | 14
Wheelock |  | 0.1 | 2250 | 2194.2765 | 3291.5336 | 5485.6913
Gentex |  | 0.2 | 1050 | 1100.3369 | 1650.565 | 2750.8423
System Sensor |  | 0.3 | 740 | 734.8082 | 1102.2521 | 1837.0206
Users Choice |  | 0.4 | 550 | 551.7725 | 827.6886 | 1379.4311
|  | 0.5 | 450 | 441.8319 | 662.7717 | 1104.5796

## Circuit Config
Circuit: | SLC 1 Devices |  |  | Max STBY Current with 10% Safety: |  | 0.2043 | Amps
2
Qty | Device |  | Timing (s) | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | Number of activated RIs; Activated RIs Current |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | Device Alarm LED Current |  |  |  |  | 0 | 0 |  |  | 0 | [5 empty] | 0
0 | Number of Activated ISOs; Activated ISOs Current |  |  |  | 0 |  | 0
0 | Number of ISOs
0 | Number of Sounder bases (ASB) (Addr.128-254)
0 | Number of Devices and Modules (Addr.1-254)
0 | Total Number of Devices, modules, ASB and ISOs. |  | Total Timing | 0 | Total Amps | 0 | 0
Circuit: | SLC 2 CARD
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
1 | SLC 2 Card |  |  | 0.06 | 0.06 | 0.06 | 0.06
[5 empty] | Total Amps | 0.06 | 0.06
Circuit: | SLC 2 Devices |  |  | Max STBY Current with 10% Safety: |  | 0.2043 | Amps
2
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  | Timing(s) | Standby | Alarm | Standby | Alarm
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | Number of activated RIs; Activated RIs Current |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
0 | Device Alarm LED Current |  |  |  |  | 0 | 0 |  |  | 0 | [5 empty] | 0
0 | Number of Activated ISOs; Activated ISOs Current |  |  |  | 0 |  | 0
0 | Number of ISOs
0 | Number of Sounder bases (ASB) (Addr.128-254)
0 | Number of Devices and Modules (Addr.1-254)
0 | Total Number of Devices, modules, ASB and ISOs. |  | Total Timing | 0 | Total Amps | 0 | 0
Circuit: | Aux Power |  |  | Max Current with 10% Safety: |  | 0.45 | Amps
2
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
[6 empty] | 0 | 0
[5 empty] | Total Amps | 0 | 0
Circuit: | MB NAC 1 |  |  | Max Current with 10% Safety: |  | 2.25 | Amps
2
Qty | Manufacture | Device |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
| Unused | - |  | 0 | 0 | 0 | 0
| Unused |  |  | 0 | 0 | 0 | 0
| Unused |  |  | 0 | 0 | 0 | 0
| Unused | - |  | 0 | 0 | 0 | 0
[6 empty] | 0 | 0
[5 empty] | Total Amps | 0 | 0
Circuit: | MB NAC 2 |  |  | Max Current with 10% Safety: |  | 2.25 | Amps
2
Qty | Manufacture | Device |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
| Unused |  |  | 0 | 0 | 0 | 0
| Unused |  |  | 0 | 0 | 0 | 0
| Unused |  |  | 0 | 0 | 0 | 0
| Unused | - |  | 0 | 0 | 0 | 0
[6 empty] | 0 | 0
[5 empty] | Total Amps | 0 | 0
Circuit: | Option Bus |  |  | Max Current with 10% Safety: |  | 0.45 | Amps
2
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0
|  |  |  | 0 | 0.0175 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0.018 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0.03 | 0 | 0
|  |  |  | 0.03 | 0 | 0 | 0
|  |  | 0 | 0 | Total Amps | 0 | 0
5
Circuit: | CITY TIE
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
0 | Local Energy Mode |  |  | 0 | 0 | 0 | 0
0 | Reverse Polarity |  |  | 0 | 0 | 0 | 0
[5 empty] | Total Amps | 0 | 0
Circuit: | NETWORK CARD
Qty | Device |  |  | Current Draw Each |  | Current Draw Total
|  |  |  | Standby | Alarm | Standby | Alarm
0 | FPE-1000-NE (Network Card 2-Ethernet) |  |  | 0 | 0 | 0 | 0
| 0 |  |  |  | Total Amps | 0 | 0
0
0.03
Edit Device Database
Edit Device Database
Edit Device Database

## Devices
Manufacture | Model | Description | Standby [in Amps] | Alarm [in Amps]
Unused | - | - | 0 | 0
Wheelock | NS-24MCW (15c) | MINI HRN/STR 24VRC WAL WHT | 0 | 0.133
Wheelock | NS-24MCW (30c) | MINI HRN/STR 24VRC WAL WHT | 0 | 0.189
Wheelock | NS-24MCW (75c) | MINI HRN/STR 24VRC WAL WHT | 0 | 0.285
Wheelock | NS-24MCW (110c) | MINI HRN/STR 24VRC WAL WHT | 0 | 0.383
Wheelock | NS-241575W (75c) | HRN/STR 24V 15/75C RED | 0 | 0.175
Wheelock | NH-12/24 | HRN SYNC VARC 12/24V RED | 0 | 0.075
Wheelock | AS-24MCW (15c) | HRN/STRB 24VARCNDL WL RED | 0 | 0.126
Wheelock | AS-24MCW (30c) | HRN/STRB 24VARCNDL WL RED | 0 | 0.18
Wheelock | AS-24MCW (75c) | HRN/STRB 24VARCNDL WL RED | 0 | 0.289
Wheelock | AS-24MCW (110c) | HRN/STRB 24VARCNDL WL RED | 0 | 0.382
Wheelock | AS-24MCWH (135c) | HRNSTB 135-185C 24V SQRED | 0 | 0.515
Wheelock | AS-24MCWH (185c) | HRNSTB 135-185C 24V SQRED | 0 | 0.7
Wheelock | AS-241575W (75c) | HRN/STR SYNC 24V 15/75C 2W | 0 | 0.178
Wheelock | AS-24MCC (15c) | HRN/STR 24V 15-95C RED | 0 | 0.135
Wheelock | AS-24MCC (30c) | HRN/STR 24V 15-95C RED | 0 | 0.19
Wheelock | AS-24MCC (75c) | HRN/STR 24V 15-95C RED | 0 | 0.305
Wheelock | AS-24MCC (95c) | HRN/STR 24V 15-95C RED | 0 | 0.4
Wheelock | AS-24MCCH (115c) | HRN/STRB 24V 115/177C RED | 0 | 0.515
Wheelock | AS-24MCCH (177c) | HRN/STRB 24V 115/177C RED | 0 | 0.7
Wheelock | ASWP-2475W (75c) | HRN/STRB 24V 75C OUTDR RD | 0 | 0.235
Wheelock | AH-24 | HRN SYNC SURF 24V RED | 0 | 0.09
Wheelock | AH-24WP-R | HRN SYNC WHTHRPRF 24V RED | 0 | 0.09
Wheelock | HS4-24MCW (15c) | HRNSTR 15-110C 24V 4W SQR | 0 | 0.196
Wheelock | HS4-24MCW (30c) | HRNSTR 15-110C 24V 4W SQR | 0 | 0.249
Wheelock | HS4-24MCW (75c) | HRNSTR 15-110C 24V 4W SQR | 0 | 0.347
Wheelock | HS4-24MCW (110c) | HRNSTR 15-110C 24V 4W SQR | 0 | 0.441
Wheelock | HS4-241575W (15c) | HRNSTR 4WIRE 24V 15/75C R | 0 | 0.239
Wheelock | HS4-24MCWH (135c) | HRNSTR135-185C 24V 4W SQR | 0 | 0.549
Wheelock | HS4-24MCWH (185c) | HRNSTR135-185C 24V 4W SQR | 0 | 0.739
Wheelock | HS-24 | HORN 24V | 0 | 0.094
Wheelock | MT-12/24 (Continuous Horn) | HRN MULTI 12/24V FLSH RED | 0 | 0.087
Wheelock | MT-12/24 (Bell) | HRN MULTI 12/24V FLSH RED | 0 | 0.051
Wheelock | MT-12/24 (March Time) | HRN MULTI 12/24V FLSH RED | 0 | 0.087
Wheelock | MT-12/24 (Temporal Horn) | HRN MULTI 12/24V FLSH RED | 0 | 0.087
Wheelock | MT-12/24 (Temporal Tone) | HRN MULTI 12/24V FLSH RED | 0 | 0.06
Wheelock | MT-12/24 (Slow Whoop) | HRN MULTI 12/24V FLSH RED | 0 | 0.092
Wheelock | MT-12/24 (Siren) | HRN MULTI 12/24V FLSH RED | 0 | 0.092
Wheelock | MT-12/24 (Hi-Lo) | HRN MULTI 12/24V FLSH RED | 0 | 0.058
Wheelock | MT-241575W (Continuous Horn, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.232
Wheelock | MT-241575W (Bell, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.196
Wheelock | MT-241575W (March Time, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.232
Wheelock | MT-241575W (Temporal Horn, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.232
Wheelock | MT-241575W (Temporal Tone, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.205
Wheelock | MT-241575W (Slow Whoop, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.237
Wheelock | MT-241575W (Siren, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.237
Wheelock | MT-241575W (Hi-Lo, 15c) | MTONESTR 24V 15/75C WL RD | 0 | 0.203
Wheelock | MT-24MCW (Continuous Horn, 15c) | STRB 24V VARC WALL RED | 0 | 0.189
Wheelock | MT-24MCW (Continuous Horn, 30c) | STRB 24V VARC WALL RED | 0 | 0.242
Wheelock | MT-24MCW (Continuous Horn, 75c) | STRB 24V VARC WALL RED | 0 | 0.34
Wheelock | MT-24MCW (Continuous Horn, 110c) | STRB 24V VARC WALL RED | 0 | 0.434
Wheelock | MT-24MCW (Bell, 15c) | STRB 24V VARC WALL RED | 0 | 0.153
Wheelock | MT-24MCW (Bell, 30c) | STRB 24V VARC WALL RED | 0 | 0.206
Wheelock | MT-24MCW (Bell, 75c) | STRB 24V VARC WALL RED | 0 | 0.304
Wheelock | MT-24MCW (Bell, 110c) | STRB 24V VARC WALL RED | 0 | 0.398
Wheelock | MT-24MCW (March Time, 15c) | STRB 24V VARC WALL RED | 0 | 0.189
Wheelock | MT-24MCW (March Time, 30c) | STRB 24V VARC WALL RED | 0 | 0.242
Wheelock | MT-24MCW (March Time, 75c) | STRB 24V VARC WALL RED | 0 | 0.34
Wheelock | MT-24MCW (March Time, 110c) | STRB 24V VARC WALL RED | 0 | 0.434
Wheelock | MT-24MCW (Temporal Horn, 15c) | STRB 24V VARC WALL RED | 0 | 0.189
Wheelock | MT-24MCW (Temporal Horn, 30c) | STRB 24V VARC WALL RED | 0 | 0.242
Wheelock | MT-24MCW (Temporal Horn, 75c) | STRB 24V VARC WALL RED | 0 | 0.34
Wheelock | MT-24MCW (Temporal Horn, 110c) | STRB 24V VARC WALL RED | 0 | 0.434
Wheelock | MT-24MCW (Temporal Tone, 15c) | STRB 24V VARC WALL RED | 0 | 0.162
Wheelock | MT-24MCW (Temporal Tone, 30c) | STRB 24V VARC WALL RED | 0 | 0.215
Wheelock | MT-24MCW (Temporal Tone, 75c) | STRB 24V VARC WALL RED | 0 | 0.313
Wheelock | MT-24MCW (Temporal Tone, 110c) | STRB 24V VARC WALL RED | 0 | 0.407
Wheelock | MT-24MCW (Slow Whoop, 15c) | STRB 24V VARC WALL RED | 0 | 0.194
Wheelock | MT-24MCW (Slow Whoop, 30c) | STRB 24V VARC WALL RED | 0 | 0.247
Wheelock | MT-24MCW (Slow Whoop, 75c) | STRB 24V VARC WALL RED | 0 | 0.345
Wheelock | MT-24MCW (Slow Whoop, 110c) | STRB 24V VARC WALL RED | 0 | 0.439
Wheelock | MT-24MCW (Siren, 15c) | STRB 24V VARC WALL RED | 0 | 0.194
Wheelock | MT-24MCW (Siren, 30c) | STRB 24V VARC WALL RED | 0 | 0.247
Wheelock | MT-24MCW (Siren, 75c) | STRB 24V VARC WALL RED | 0 | 0.345
Wheelock | MT-24MCW (Siren, 110c) | STRB 24V VARC WALL RED | 0 | 0.439
Wheelock | MT-24MCW (Hi-Lo, 15c) | STRB 24V VARC WALL RED | 0 | 0.16
Wheelock | MT-24MCW (Hi-Lo, 30c) | STRB 24V VARC WALL RED | 0 | 0.213
Wheelock | MT-24MCW (Hi-Lo, 75c) | STRB 24V VARC WALL RED | 0 | 0.311
Wheelock | MT-24MCW (Hi-Lo, 110c) | STRB 24V VARC WALL RED | 0 | 0.405
Wheelock | MTWP-2475W (Continuous Horn, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.309
Wheelock | MTWP-2475W (Bell,75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.273
Wheelock | MTWP-2475W (March Time, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.309
Wheelock | MTWP-2475W (Temporal Horn, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.309
Wheelock | MTWP-2475W (Temporal Tone, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.282
Wheelock | MTWP-2475W (Slow Whoop, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.314
Wheelock | MTWP-2475W (Siren, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.314
Wheelock | MTWP-2475W (Hi-Lo, 75c) | WTHRPRF MULTI STR 24V 75C | 0 | 0.28
Wheelock | AMT-12/24 (Continuous Horn) | MLTITONE 12/24V FL RED | 0 | 0.092
Wheelock | AMT-12/24 (Bell) | MLTITONE 12/24V FL RED | 0 | 0.04
Wheelock | AMT-12/24 (March Time) | MLTITONE 12/24V FL RED | 0 | 0.092
Wheelock | AMT-12/24 (Temporal Horn) | MLTITONE 12/24V FL RED | 0 | 0.092
Wheelock | AMT-12/24 (Temporal Tone) | MLTITONE 12/24V FL RED | 0 | 0.051
Wheelock | AMT-12/24 (Slow Whoop) | MLTITONE 12/24V FL RED | 0 | 0.092
Wheelock | AMT-12/24 (Siren) | MLTITONE 12/24V FL RED | 0 | 0.078
Wheelock | AMT-12/24 (Hi-Lo) | MLTITONE 12/24V FL RED | 0 | 0.049
Wheelock | AMT-12/24 (Vibrating Chime) | MLTITONE 12/24V FL RED | 0 | 0.044
Wheelock | AMT-241575W (Continuous Horn, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.237
Wheelock | AMT-241575W (Bell, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.185
Wheelock | AMT-241575W (March Time, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.237
Wheelock | AMT-241575W (Temporal Horn, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.237
Wheelock | AMT-241575W (Temporal Tone, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.196
Wheelock | AMT-241575W (Slow Whoop, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.237
Wheelock | AMT-241575W (Siren, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.223
Wheelock | AMT-241575W (Hi-Lo, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.194
Wheelock | AMT-241575W (Vibrating Chime, 15c) | HRN/STR MULTI 24V 15/75C R | 0 | 0.189
Wheelock | AMT-24MCW (Continuous Horn, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.194
Wheelock | AMT-24MCW (Continuous Horn, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.247
Wheelock | AMT-24MCW (Continuous Horn, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.345
Wheelock | AMT-24MCW (Continuous Horn, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.439
Wheelock | AMT-24MCW (Bell, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.142
Wheelock | AMT-24MCW (Bell, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.195
Wheelock | AMT-24MCW (Bell, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.293
Wheelock | AMT-24MCW (Bell, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.387
Wheelock | AMT-24MCW (March Time, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.194
Wheelock | AMT-24MCW (March Time, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.247
Wheelock | AMT-24MCW (March Time, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.345
Wheelock | AMT-24MCW (March Time, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.439
Wheelock | AMT-24MCW (Temporal Horn, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.194
Wheelock | AMT-24MCW (Temporal Horn, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.247
Wheelock | AMT-24MCW (Temporal Horn, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.345
Wheelock | AMT-24MCW (Temporal Horn, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.439
Wheelock | AMT-24MCW (Temporal Tone, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.153
Wheelock | AMT-24MCW (Temporal Tone, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.206
Wheelock | AMT-24MCW (Temporal Tone, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.304
Wheelock | AMT-24MCW (Temporal Tone, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.398
Wheelock | AMT-24MCW (Slow Whoop, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.194
Wheelock | AMT-24MCW (Slow Whoop, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.247
Wheelock | AMT-24MCW (Slow Whoop, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.345
Wheelock | AMT-24MCW (Slow Whoop, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.439
Wheelock | AMT-24MCW (Siren, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.18
Wheelock | AMT-24MCW (Siren, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.233
Wheelock | AMT-24MCW (Siren, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.331
Wheelock | AMT-24MCW (Siren, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.425
Wheelock | AMT-24MCW (Hi-Lo, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.151
Wheelock | AMT-24MCW (Hi-Lo, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.204
Wheelock | AMT-24MCW (Hi-Lo, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.302
Wheelock | AMT-24MCW (Hi-Lo, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.396
Wheelock | AMT-24MCW (Vibrating Chime, 15c) | STRB MULTI 24V 15-110C RD | 0 | 0.146
Wheelock | AMT-24MCW (Vibrating Chime, 30c) | STRB MULTI 24V 15-110C RD | 0 | 0.199
Wheelock | AMT-24MCW (Vibrating Chime, 75c) | STRB MULTI 24V 15-110C RD | 0 | 0.297
Wheelock | AMT-24MCW (Vibrating Chime, 110c) | STRB MULTI 24V 15-110C RD | 0 | 0.391
Wheelock | MIZ-24S | HR MINI SGL GANG WALL RED | 0 | 0.043
Wheelock | RSS-24MCW (15c) | STRB 24V VARC WALL RED | 0 | 0.102
Wheelock | RSS-24MCW (30c) | STRB 24V VARC WALL RED | 0 | 0.155
Wheelock | RSS-24MCW (75c) | STRB 24V VARC WALL RED | 0 | 0.253
Wheelock | RSS-24MCW (110c) | STRB 24V VARC WALL RED | 0 | 0.347
Wheelock | RSS-241575W (15c) | STRB SYNC 15/75C 24V RED | 0 | 0.145
Wheelock | RSS-24MCC (15c) | STROBE 15-95C 24V SQ WH | 0 | 0.11
Wheelock | RSS-24MCC (30c) | STROBE 15-95C 24V SQ WH | 0 | 0.17
Wheelock | RSS-24MCC (75c) | STROBE 15-95C 24V SQ WH | 0 | 0.28
Wheelock | RSS-24MCC (95c) | STROBE 15-95C 24V SQ WH | 0 | 0.375
Wheelock | RSS-24MCCR (15c) | STROBE24V 15-95C CEIL WHT | 0 | 0.11
Wheelock | RSS-24MCCR (30c) | STROBE24V 15-95C CEIL WHT | 0 | 0.17
Wheelock | RSS-24MCCR (75c) | STROBE24V 15-95C CEIL WHT | 0 | 0.28
Wheelock | RSS-24MCCR (95c) | STROBE24V 15-95C CEIL WHT | 0 | 0.375
Wheelock | RSS-24MCCH (115c) | STRB 115-177C 24V WHT | 0 | 0.455
Wheelock | RSS-24MCCH (177c) | STRB 115-177C 24V WHT | 0 | 0.645
Wheelock | RSS-24MCCHR (115c) | STRB 115-177C 24V RND WHT | 0 | 0.455
Wheelock | RSS-24MCCHR (177c) | STRB 115-177C 24V RND WHT | 0 | 0.645
Wheelock | RSS-24MCWH (135c) | STR 135/185C WALL RED | 0 | 0.455
Wheelock | RSS-24MCWH (185c) | STR 135/185C WALL RED | 0 | 0.645
Wheelock | RSSWP-2475W (75c) | STR24V WPRF 75C RED | 0 | 0.222
Wheelock | RSSP-24MCW (15c) | STR 24V 15-110C RED | 0 | 0.102
Wheelock | RSSP-24MCW (30c) | STR 24V 15-110C RED | 0 | 0.155
Wheelock | RSSP-24MCW (75c) | STR 24V 15-110C RED | 0 | 0.253
Wheelock | RSSP-24MCW (110c) | STR 24V 15-110C RED | 0 | 0.347
Wheelock | RSSP-241575W (15c) | STRB PLATE 24V 15/75C RED | 0 | 0.145
Wheelock | RSSP-24MCWH (135c) | RETF STRB 135-185C 24V R | 0 | 0.455
Wheelock | RSSP-24MCWH (185c) | RETF STRB 135-185C 24V R | 0 | 0.645
Wheelock | CH70-24MCW (15c) | CHM/STRB 24VARC WALL RED | 0 | 0.124
Wheelock | CH70-24MCW (30c) | CHM/STRB 24VARC WALL RED | 0 | 0.177
Wheelock | CH70-24MCW (75c) | CHM/STRB 24VARC WALL RED | 0 | 0.275
Wheelock | CH70-24MCW (110c) | CHM/STRB 24VARC WALL RED | 0 | 0.369
Wheelock | CH70-24MCWH (135c) | CHMSTR135-185C 24V SQ RD | 0 | 0.477
Wheelock | CH70-24MCWH (185c) | CHMSTR135-185C 24V SQ RD | 0 | 0.667
Wheelock | CH70-241575W (15c) | CHMSTR 15/75C SQ WALL RD | 0 | 0.167
Wheelock | CH90-24MCC (15c) | CHMSTR 24V 15-95C RN RD | 0 | 0.132
Wheelock | CH90-24MCC (30c) | CHMSTR 24V 15-95C RN RD | 0 | 0.192
Wheelock | CH90-24MCC (75c) | CHMSTR 24V 15-95C RN RD | 0 | 0.302
Wheelock | CH90-24MCC (95c) | CHMSTR 24V 15-95C RN RD | 0 | 0.397
Wheelock | CH90-24MCCH (115c) | CHMSTB 115-177C 24V RND W | 0 | 0.477
Wheelock | CH90-24MCCH (177c) | CHMSTB 115-177C 24V RND W | 0 | 0.667
Wheelock | CH70-24 | CHIME 24V SQ RED | 0 | 0.022
Wheelock | CH90-24 | CHIME 24V ROUND WHT | 0 | 0.022
Wheelock | MB-G6-24 | MOTOR BELL 24V 6IN RED | 0 | 0.056
Wheelock | MB-G10-24 | MOTOR BELL 24V 10IN RED | 0 | 0.056
Wheelock | E50-241575W (15c) | SPK STR SYNC 15/75C WAL RD | 0 | 0.0145
Wheelock | E50-24MCW (15c) | SPK STR 24V VARC WALL RED | 0 | 0.0102
Wheelock | E50-24MCW (30c) | SPK STR 24V VARC WALL RED | 0 | 0.0155
Wheelock | E50-24MCW (75c) | SPK STR 24V VARC WALL RED | 0 | 0.0253
Wheelock | E50-24MCW (110c) | SPK STR 24V VARC WALL RED | 0 | 0.0347
Wheelock | E50-24MCWH (135c) | SPK/STR 135-185C 24V RED | 0 | 0.0455
Wheelock | E50-24MCWH (185c) | SPK/STR 135-185C 24V RED | 0 | 0.0645
Wheelock | E70-24MCW (15c) | SPK STR 24V VARC WALL RED | 0 | 0.102
Wheelock | E70-24MCW (30c) | SPK STR 24V VARC WALL RED | 0 | 0.155
Wheelock | E70-24MCW (75c) | SPK STR 24V VARC WALL RED | 0 | 0.253
Wheelock | E70-24MCW (110c) | SPK STR 24V VARC WALL RED | 0 | 0.347
Wheelock | E70-241575W (15c) | SPK STR SYNC 15/75C WAL RD | 0 | 0.145
Wheelock | E70-24MCWH (135c) | SPKST2W 135-185CD 24V SQR | 0 | 0.455
Wheelock | E70-24MCWH (185c) | SPKST2W 135-185CD 24V SQR | 0 | 0.645
Wheelock | E90-24MCC (15c) | SPKSTRB 15-95CD 24VRND WH | 0 | 0.11
Wheelock | E90-24MCC (30c) | SPKSTRB 15-95CD 24VRND WH | 0 | 0.17
Wheelock | E90-24MCC (75c) | SPKSTRB 15-95CD 24VRND WH | 0 | 0.28
Wheelock | E90-24MCC (95c) | SPKSTRB 15-95CD 24VRND WH | 0 | 0.375
Wheelock | E90-24MCCH (115c) | SPKSTRB 115-177CD 24VRNDW | 0 | 0.455
Wheelock | E90-24MCCH (177c) | SPKSTRB 115-177CD 24VRNDW | 0 | 0.645
Wheelock | ET70-24MCW (15c) | SPK STR 8W VARC WALL RED | 0 | 0.102
Wheelock | ET70-24MCW (30c) | SPK STR 8W VARC WALL RED | 0 | 0.155
Wheelock | ET70-24MCW (75c) | SPK STR 8W VARC WALL RED | 0 | 0.253
Wheelock | ET70-24MCW (110c) | SPK STR 8W VARC WALL RED | 0 | 0.347
Wheelock | ET70-241575W (15c) | SPKR STRB SYNC 1575C RED | 0 | 0.145
Wheelock | ET70-24MCWH (135c) | SPKST8W 135-185CD 24V SQR | 0 | 0.455
Wheelock | ET70-24MCWH (185c) | SPKST8W 135-185CD 24V SQR | 0 | 0.645
Wheelock | ET70WP-2475W (180c) | SPKR/STR 75C WP 1/8-8W-RD | 0 | 0.222
Wheelock | ET90-24MCC (15c) | SPKSTR 8W 15-95C RNDWHT | 0 | 0.11
Wheelock | ET90-24MCC (30c) | SPKSTR 8W 15-95C RNDWHT | 0 | 0.17
Wheelock | ET90-24MCC (75c) | SPKSTR 8W 15-95C RNDWHT | 0 | 0.28
Wheelock | ET90-24MCC (95c) | SPKSTR 8W 15-95C RNDWHT | 0 | 0.375
Wheelock | ET90-24MCCH (115c) | SPKSTR8W 115/177C RND WHT | 0 | 0.455
Wheelock | ET90-24MCCH (177c) | SPKSTR8W 115/177C RND WHT | 0 | 0.645
Wheelock | ET80-241575W (15c) | SPKR/STRB FLSH 15/75C RED | 0 | 0.09
Wheelock | ET80-24MCW (15c) | SPKR/STRB FLSH VARC RED | 0 | 0.102
Wheelock | ET80-24MCW (30c) | SPKR/STRB FLSH VARC RED | 0 | 0.155
Wheelock | ET80-24MCW (75c) | SPKR/STRB FLSH VARC RED | 0 | 0.253
Wheelock | ET80-24MCW (110c) | SPKR/STRB FLSH VARC RED | 0 | 0.347
Wheelock | ET80-24MCWH (135c) | SPKR/STRB SYNC 135/185C R | 0 | 0.455
Wheelock | ET80-24MCWH (185c) | SPKR/STRB SYNC 135/185C R | 0 | 0.645
Wheelock | S8-24MCC (15c) | SPK RND SUPV 15-95C WHT | 0 | 0.065
Wheelock | S8-24MCC (30c) | SPK RND SUPV 15-95C WHT | 0 | 0.105
Wheelock | S8-24MCC (75c) | SPK RND SUPV 15-95C WHT | 0 | 0.189
Wheelock | S8-24MCC (95c) | SPK RND SUPV 15-95C WHT | 0 | 0.249
Wheelock | S8-24MCCH (115c) | SP 24/70V 8RND 115/177C W | 0 | 0.3
Wheelock | S8-24MCCH (177c) | SP 24/70V 8RND 115/177C W | 0 | 0.42
Wheelock | W-HNR/W (Low) | WALL-MOUNT HORN, 12/24 V, RED/WHITE | 0 | 0.054
Wheelock | W-HNR/W (Medium) | WALL-MOUNT HORN, 12/24 V, RED/WHITE | 0 | 0.074
Wheelock | W-HNR/W (High) | WALL-MOUNT HORN, 12/24 V, RED/WHITE | 0 | 0.086
Wheelock | W-HSR/W (Low, 15 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.106
Wheelock | W-HSR/W (Low, 15/75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.12
Wheelock | W-HSR/W (Low, 30 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.12
Wheelock | W-HSR/W (Low, 75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.196
Wheelock | W-HSR/W (Low, 95 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.235
Wheelock | W-HSR/W (Low, 110 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.265
Wheelock | W-HSR/W (Low, 135 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.331
Wheelock | W-HSR/W (Low, 185 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.375
Wheelock | W-HSR/W (Medium, 15 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.112
Wheelock | W-HSR/W (Medium, 15/75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.126
Wheelock | W-HSR/W (Medium, 30 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.126
Wheelock | W-HSR/W (Medium, 75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.201
Wheelock | W-HSR/W (Medium, 95 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.247
Wheelock | W-HSR/W (Medium, 110 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.272
Wheelock | W-HSR/W (Medium, 135 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.34
Wheelock | W-HSR/W (Medium, 185 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.378
Wheelock | W-HSR/W (High, 15 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.133
Wheelock | W-HSR/W (High, 15/75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.138
Wheelock | W-HSR/W (High, 30 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.138
Wheelock | W-HSR/W (High, 75 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.216
Wheelock | W-HSR/W (High, 95 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.258
Wheelock | W-HSR/W (High, 110 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.289
Wheelock | W-HSR/W (High, 135 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.357
Wheelock | W-HSR/W (High, 185 cd) | WALL-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.384
Wheelock | W-HSRC/WC (Low, 15 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.106
Wheelock | W-HSRC/WC (Low, 30 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.12
Wheelock | W-HSRC/WC (Low, 60 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.186
Wheelock | W-HSRC/WC (Low, 75 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.196
Wheelock | W-HSRC/WC (Low, 95 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.235
Wheelock | W-HSRC/WC (Low, 115 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.265
Wheelock | W-HSRC/WC (Low, 150 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.331
Wheelock | W-HSRC/WC (Low, 177 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.375
Wheelock | W-HSRC/WC (Medium, 15 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.112
Wheelock | W-HSRC/WC (Medium, 30 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.126
Wheelock | W-HSRC/WC (Medium, 60 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.202
Wheelock | W-HSRC/WC (Medium, 75 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.201
Wheelock | W-HSRC/WC (Medium, 95 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.247
Wheelock | W-HSRC/WC (Medium, 115 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.272
Wheelock | W-HSRC/WC (Medium, 150 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.34
Wheelock | W-HSRC/WC (Medium, 177 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.378
Wheelock | W-HSRC/WC (High, 15 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.131
Wheelock | W-HSRC/WC (High, 30 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.138
Wheelock | W-HSRC/WC (High, 60 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.22
Wheelock | W-HSRC/WC (High, 75 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.216
Wheelock | W-HSRC/WC (High, 95 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.258
Wheelock | W-HSRC/WC (High, 115 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.289
Wheelock | W-HSRC/WC (High, 150 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.357
Wheelock | W-HSRC/WC (High, 177 cd) | CEILING-MOUNT MULTI-CANDELA HORE STROBE, 12/24 V, RED/WHITE | 0 | 0.384
Wheelock | W-STR/W (15 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.083
Wheelock | W-STR/W (15/75 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.105
Wheelock | W-STR/W (30 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.105
Wheelock | W-STR/W (75 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.185
Wheelock | W-STR/W (95 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.223
Wheelock | W-STR/W (110 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.269
Wheelock | W-STR/W (135 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.328
Wheelock | W-STR/W (185 cd) | WALL-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.372
Wheelock | W-STRC/WC (15 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.083
Wheelock | W-STRC/WC (30 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.105
Wheelock | W-STRC/WC (60 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.166
Wheelock | W-STRC/WC (75 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.185
Wheelock | W-STRC/WC (95 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.223
Wheelock | W-STRC/WC (115 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.256
Wheelock | W-STRC/WC (150 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.328
Wheelock | W-STRC/WC (177 cd) | CEILING-MOUNT MULTI-CANDELA STROBE, 12/24 V, RED/WHITE | 0 | 0.372
Gentex | GES24-15W (15c) | STR24V15C RED IN | 0 | 0.113
Gentex | GES24-15/75W (15/75c) | STR24V15/75C WHT IN | 0 | 0.135
Gentex | GES24-30W (30c) | STR24V30C WHT IN | 0 | 0.135
Gentex | GES24-60W (60c) | STR24V60C RED IN | 0 | 0.186
Gentex | GES24-75W (75c) | STR24V75C RED IN | 0 | 0.245
Gentex | GES24-110W (110c) | STR24V110C WHT IN | 0 | 0.313
Gentex | GEH24 (Cont Horn, 2400Hz) | HRN 24V WHT IN | 0 | 0.048
Gentex | GEH24 (Cont Horn, Mech) | HRN 24V WHT IN | 0 | 0.044
Gentex | GEH24 (Temp Horn, 2400Hz) | HRN 24V WHT IN | 0 | 0.048
Gentex | GEH24 (Temp Horn, Mech) | HRN 24V WHT IN | 0 | 0.044
Gentex | GEH24 (Cont Chime) | HRN 24V WHT IN | 0 | 0.03
Gentex | GEH24 (Temp Chime) | HRN 24V WHT IN | 0 | 0.03
Gentex | GEH24 (Whoop) | HRN 24V WHT IN | 0 | 0.062
Gentex | GEC3-24W (Cont Horn, 2400Hz, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.161
Gentex | GEC3-24W (Cont Horn, Mech, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.157
Gentex | GEC3-24W (Temp Horn, 2400Hz, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.161
Gentex | GEC3-24W (Temp Horn, Mech, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.157
Gentex | GEC3-24W (Continuous Chime, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.143
Gentex | GEC3-24W (Temporal Chime, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.143
Gentex | GEC3-24W (Whoop, 15c) | HN/ST 24V 15-110C WALL RD | 0 | 0.175
Gentex | GEC3-24W (Cont Horn, 2400Hz, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.183
Gentex | GEC3-24W (Cont Horn, Mech, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.179
Gentex | GEC3-24W (Temp Horn, 2400Hz, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.183
Gentex | GEC3-24W (Temp Horn, Mech, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.179
Gentex | GEC3-24W (Continuous Chime, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.165
Gentex | GEC3-24W (Temporal Chime, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.165
Gentex | GEC3-24W (Whoop, 30c) | HN/ST 24V 15-110C WALL RD | 0 | 0.197
Gentex | GEC3-24W (Cont Horn, 2400Hz, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.234
Gentex | GEC3-24W (Cont Horn, Mech, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.23
Gentex | GEC3-24W (Temp Horn, 2400Hz, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.234
Gentex | GEC3-24W (Temp Horn, Mech, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.23
Gentex | GEC3-24W (Continuous Chime, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.216
Gentex | GEC3-24W (Temporal Chime, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.216
Gentex | GEC3-24W (Whoop, 60c) | HN/ST 24V 15-110C WALL RD | 0 | 0.248
Gentex | GEC3-24W (Cont Horn, 2400Hz, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.293
Gentex | GEC3-24W (Cont Horn, Mech, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.289
Gentex | GEC3-24W (Temp Horn, 2400Hz, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.293
Gentex | GEC3-24W (Temp Horn, Mech, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.289
Gentex | GEC3-24W (Continuous Chime, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.275
Gentex | GEC3-24W (Temporal Chime, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.275
Gentex | GEC3-24W (Whoop, 75c) | HN/ST 24V 15-110C WALL RD | 0 | 0.307
Gentex | GEC3-24W (Cont Horn, 2400Hz, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.361
Gentex | GEC3-24W (Cont Horn, Mech, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.357
Gentex | GEC3-24W (Temp Horn, 2400Hz, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.361
Gentex | GEC3-24W (Temp Horn, Mech, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.357
Gentex | GEC3-24W (Continuous Chime, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.343
Gentex | GEC3-24W (Temporal Chime, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.343
Gentex | GEC3-24W (Whoop, 110c) | HN/ST 24V 15-110C WALL RD | 0 | 0.375
Gentex | GEC24-15W (Cont Horn, 2400Hz, 15c) | HRN/STR24V15C RED IN | 0 | 0.161
Gentex | GEC24-15W (Cont Horn, Mech, 15c) | HRN/STR24V15C RED IN | 0 | 0.157
Gentex | GEC24-15W (Temp Horn, 2400Hz, 15c) | HRN/STR24V15C RED IN | 0 | 0.161
Gentex | GEC24-15W (Temp Horn, Mech, 15c) | HRN/STR24V15C RED IN | 0 | 0.157
Gentex | GEC24-15W (Continuous Chime, 15c) | HRN/STR24V15C RED IN | 0 | 0.143
Gentex | GEC24-15W (Temp Chime, 15c) | HRN/STR24V15C RED IN | 0 | 0.143
Gentex | GEC24-15W (Whoop, 15c) | HRN/STR24V15C RED IN | 0 | 0.175
Gentex | GEC24-15/75W (CHorn, 2400Hz, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.183
Gentex | GEC24-15/75W (Cont Horn, Mech, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.179
Gentex | GEC24-15/75W (T Horn, 2400Hz, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.183
Gentex | GEC24-15/75W (T Horn, Mech, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.179
Gentex | GEC24-15/75W (Cont Chime, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.165
Gentex | GEC24-15/75W (Temp Chime, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.165
Gentex | GEC24-15/75W (Whoop, 15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.197
Gentex | GEC24-30W (CHorn, 2400Hz, 30c) | HRN/STR24V30C RED IN | 0 | 0.183
Gentex | GEC24-30W (Cont Horn, Mech, 30c) | HRN/STR24V30C RED IN | 0 | 0.179
Gentex | GEC24-30W (T Horn, 2400Hz, 30c) | HRN/STR24V30C RED IN | 0 | 0.183
Gentex | GEC24-30W (T Horn, Mech, 30c) | HRN/STR24V30C RED IN | 0 | 0.179
Gentex | GEC24-30W (Cont Chime, 30c) | HRN/STR24V30C RED IN | 0 | 0.165
Gentex | GEC24-30W (Temp Chime, 30c) | HRN/STR24V30C RED IN | 0 | 0.165
Gentex | GEC24-30W (Whoop, 30c) | HRN/STR24V30C RED IN | 0 | 0.197
Gentex | GEC24-60W (CHorn, 2400Hz, 60c) | HRN/STR24V60C WHT IN | 0 | 0.234
Gentex | GEC24-60W (Cont Horn, Mech, 60c) | HRN/STR24V60C WHT IN | 0 | 0.23
Gentex | GEC24-60W (T Horn, 2400Hz, 60c) | HRN/STR24V60C WHT IN | 0 | 0.234
Gentex | GEC24-60W (T Horn, Mech, 60c) | HRN/STR24V60C WHT IN | 0 | 0.23
Gentex | GEC24-60W (Cont Chime, 60c) | HRN/STR24V60C WHT IN | 0 | 0.216
Gentex | GEC24-60W (Temp Chime, 60c) | HRN/STR24V60C WHT IN | 0 | 0.216
Gentex | GEC24-60W (Whoop, 60c) | HRN/STR24V60C WHT IN | 0 | 0.248
Gentex | GEC24-75W (CHorn, 2400Hz, 75c) | HRN/STR24V75C RED IN | 0 | 0.293
Gentex | GEC24-75W (Cont Horn, Mech, 75c) | HRN/STR24V75C RED IN | 0 | 0.289
Gentex | GEC24-75W (T Horn, 2400Hz, 75c) | HRN/STR24V75C RED IN | 0 | 0.293
Gentex | GEC24-75W (T Horn, Mech, 75c) | HRN/STR24V75C RED IN | 0 | 0.289
Gentex | GEC24-75W (Cont Chime, 75c) | HRN/STR24V75C RED IN | 0 | 0.275
Gentex | GEC24-75W (Temp Chime, 75c) | HRN/STR24V75C RED IN | 0 | 0.275
Gentex | GEC24-75W (Whoop, 75c) | HRN/STR24V75C RED IN | 0 | 0.307
Gentex | GEC24-110W (CHorn, 2400Hz, 110c) | HRN/STR24V110C RED IN | 0 | 0.361
Gentex | GEC24-110W (Cont Horn, Mech, 110c) | HRN/STR24V110C RED IN | 0 | 0.357
Gentex | GEC24-110W (T Horn, 2400Hz, 110c) | HRN/STR24V110C RED IN | 0 | 0.361
Gentex | GEC24-110W (T Horn, Mech, 110c) | HRN/STR24V110C RED IN | 0 | 0.357
Gentex | GEC24-110W (Cont Chime, 110c) | HRN/STR24V110C RED IN | 0 | 0.343
Gentex | GEC24-110W (Temp Chime, 110c) | HRN/STR24V110C RED IN | 0 | 0.343
Gentex | GEC24-110W (Whoop, 110c) | HRN/STR24V110C RED IN | 0 | 0.375
Gentex | GESR24WW (Temp Horn, 2400Hz, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.21
Gentex | GESR24WW (Temp Horn, Mech, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.206
Gentex | GESR24WW (Temp Chime, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.192
Gentex | GESR24WW (Cont Horn, 2400Hz, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.21
Gentex | GESR24WW (Cont Horn, Mech, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.206
Gentex | GESR24WW (Cont Chime, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.192
Gentex | GESR24WW (Whoop, 15c) | 15-110CD HRN STRB WHT WAL | 0 | 0.224
Gentex | GESR24WW (Temp Horn, 2400Hz, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.224
Gentex | GESR24WW (Temp Horn, Mech, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.22
Gentex | GESR24WW (Temp Chime, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.206
Gentex | GESR24WW (Cont Horn, 2400Hz, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.224
Gentex | GESR24WW (Cont Horn, Mech, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.22
Gentex | GESR24WW (Cont Chime, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.206
Gentex | GESR24WW (Whoop, 30c) | 15-110CD HRN STRB WHT WAL | 0 | 0.238
Gentex | GESR24WW (Temp Horn, 2400Hz, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.314
Gentex | GESR24WW (Temp Horn, Mech, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.31
Gentex | GESR24WW (Temp Chime, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.296
Gentex | GESR24WW (Cont Horn, 2400Hz, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.314
Gentex | GESR24WW (Cont Horn, Mech, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.31
Gentex | GESR24WW (Cont Chime, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.296
Gentex | GESR24WW (Whoop, 60c) | 15-110CD HRN STRB WHT WAL | 0 | 0.328
Gentex | GESR24WW (Temp Horn, 2400Hz, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.359
Gentex | GESR24WW (Temp Horn, Mech, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.355
Gentex | GESR24WW (Temp Chime, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.341
Gentex | GESR24WW (Cont Horn, 2400Hz, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.359
Gentex | GESR24WW (Cont Horn, Mech, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.355
Gentex | GESR24WW (Cont Chime, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.341
Gentex | GESR24WW (Whoop, 75c) | 15-110CD HRN STRB WHT WAL | 0 | 0.373
Gentex | GESR24WW (Temp Horn, 2400Hz, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.467
Gentex | GESR24WW (Temp Horn, Mech, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.463
Gentex | GESR24WW (Temp Chime, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.449
Gentex | GESR24WW (Cont Horn, 2400Hz, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.467
Gentex | GESR24WW (Cont Horn, Mech, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.463
Gentex | GESR24WW (Cont Chime, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.449
Gentex | GESR24WW (Whoop, 110c) | 15-110CD HRN STRB WHT WAL | 0 | 0.481
Gentex | GES3-24W (15c) | STRB 24V 15-110C WALL WHT | 0 | 0.113
Gentex | GES3-24W (30c) | STRB 24V 15-110C WALL WHT | 0 | 0.135
Gentex | GES3-24W (60c) | STRB 24V 15-110C WALL WHT | 0 | 0.186
Gentex | GES3-24W (75c) | STRB 24V 15-110C WALL WHT | 0 | 0.245
Gentex | GES3-24W (110c) | STRB 24V 15-110C WALL WHT | 0 | 0.313
Gentex | GX91 | HRN 12/24V NO SYNC RED | 0 | 0.013
Gentex | GX93 | HRN 12/24V SYNC/AVS RED | 0 | 0.02
Gentex | HS24-15W (15c) | HRN/STR24V15C RED IN | 0 | 0.129
Gentex | HS24-15/75W (15/75c) | HRN/STR24V15/75C RED IN | 0 | 0.168
Gentex | HS24-30W (30c) | HRN/STR24V30C RED IN | 0 | 0.168
Gentex | HS24-60W (60c) | HRN/STR24V60C RED IN | 0 | 0.221
Gentex | HS24-75W (75c) | HRN/STR24V75C RED IN | 0 | 0.253
Gentex | HS24-110W (110c) | HRN/STR24V110C RED IN | 0 | 0.301
Gentex | GCSR24CW (Temp Horn, 2400Hz, 15c) | 15-110CD HRN STR WHT CEIL | 0 | 0.228
Gentex | GCSR24CW (Temp Horn, Mech, 15c) | 15-110CD HRN STR WHT CEIL | 0 | 0.226
Gentex | GCSR24CW (Cont Horn, 2400Hz, 15c) | 15-110CD HRN STR WHT CEIL | 0 | 0.228
Gentex | GCSR24CW (Cont Horn, Mech, 15c) | 15-110CD HRN STR WHT CEIL | 0 | 0.226
Gentex | GCSR24CW (Temp Horn, 2400Hz, 30c) | 15-110CD HRN STR WHT CEIL | 0 | 0.235
Gentex | GCSR24CW (Temp Horn, Mech, 30c) | 15-110CD HRN STR WHT CEIL | 0 | 0.233
Gentex | GCSR24CW (Cont Horn, 2400Hz, 30c) | 15-110CD HRN STR WHT CEIL | 0 | 0.235
Gentex | GCSR24CW (Cont Horn, Mech, 30c) | 15-110CD HRN STR WHT CEIL | 0 | 0.233
Gentex | GCSR24CW (Temp Horn, 2400Hz, 75c) | 15-110CD HRN STR WHT CEIL | 0 | 0.379
Gentex | GCSR24CW (Temp Horn, Mech, 75c) | 15-110CD HRN STR WHT CEIL | 0 | 0.377
Gentex | GCSR24CW (Cont Horn, 2400Hz, 75c) | 15-110CD HRN STR WHT CEIL | 0 | 0.379
Gentex | GCSR24CW (Cont Horn, Mech, 75c) | 15-110CD HRN STR WHT CEIL | 0 | 0.377
Gentex | GCSR24CW (Temp Horn, 2400Hz, 95c) | 15-110CD HRN STR WHT CEIL | 0 | 0.484
Gentex | GCSR24CW (Temp Horn, Mech, 95c) | 15-110CD HRN STR WHT CEIL | 0 | 0.482
Gentex | GCSR24CW (Cont Horn, 2400Hz, 95c) | 15-110CD HRN STR WHT CEIL | 0 | 0.484
Gentex | GCSR24CW (Cont Horn, Mech, 95c) | 15-110CD HRN STR WHT CEIL | 0 | 0.482
Gentex | GCSR24CW (Temp Horn, 2400Hz, 115c) | 15-110CD HRN STR WHT CEIL | 0 | 0.539
Gentex | GCSR24CW (Temp Horn, Mech, 115c) | 15-110CD HRN STR WHT CEIL | 0 | 0.537
Gentex | GCSR24CW (Cont Horn, 2400Hz, 115c) | 15-110CD HRN STR WHT CEIL | 0 | 0.539
Gentex | GCSR24CW (Cont Horn, Mech, 115c) | 15-110CD HRN STR WHT CEIL | 0 | 0.537
Gentex | WGES24-75WR (75c) | STRB WTHRPR 75C W/GOE RED | 0 | 0.245
Gentex | WGEC24-75W (Cont Horn, 2400Hz, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.293
Gentex | WGEC24-75W (Cont Horn, Mech, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.289
Gentex | WGEC24-75W (Temp Horn, 2400Hz, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.293
Gentex | WGEC24-75W (Temp Horn, Mech, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.289
Gentex | WGEC24-75W (Cont Chime, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.275
Gentex | WGEC24-75W (Temp Chime, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.275
Gentex | WGEC24-75W (Whoop, 75c) | HRN/STRB 75C W/GOE RED | 0 | 0.307
Gentex | SSPK24-15W (15c) | SP/ST 1/8-4W 15C WALL RED | 0 | 0.113
Gentex | SSPK24-1575W (15/75c) | SP/ST 1/8-4W 1575C WAL RD | 0 | 0.245
Gentex | SSPK24-30W (30c) | SP/ST 1/8-4W 30C WALL RED | 0 | 0.135
Gentex | SSPK24-60W (60c) | SP/ST 1/8-4W 60C WALL WHT | 0 | 0.186
Gentex | SSPK24-75W (75c) | SP/ST 1/8-4W 1575C WAL WH | 0 | 0.245
Gentex | SSPK24-110W (110c) | SP/ST 1/8-4W 110C WALL RD | 0 | 0.313
Gentex | GCC24-CR (Temp Horn, 2400Hz, 15c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.117
Gentex | GCC24-CR (Temp Horn, 2400Hz, 30c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.133
Gentex | GCC24-CR (Temp Horn, 2400Hz, 75c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.221
Gentex | GCC24-CR (Temp Horn, 2400Hz, 95c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.245
Gentex | GCC24-CR (Temp Horn, 2400Hz, 115c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.259
Gentex | GCC24-CR (Temp Horn, 2400Hz, 150c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.331
Gentex | GCC24-CR (Temp Horn, Mech, 15c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.115
Gentex | GCC24-CR (Temp Horn, Mech, 30c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.131
Gentex | GCC24-CR (Temp Horn, Mech, 75c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.219
Gentex | GCC24-CR (Temp Horn, Mech, 95c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.243
Gentex | GCC24-CR (Temp Horn, Mech, 115c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.257
Gentex | GCC24-CR (Temp Horn, Mech, 150c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.329
Gentex | GCC24-CR (Cont Horn, 2400Hz, 15c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.117
Gentex | GCC24-CR (Cont Horn, 2400Hz, 30c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.133
Gentex | GCC24-CR (Cont Horn, 2400Hz, 75c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.221
Gentex | GCC24-CR (Cont Horn, 2400Hz, 95c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.245
Gentex | GCC24-CR (Cont Horn, 2400Hz, 115c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.259
Gentex | GCC24-CR (Cont Horn, 2400Hz, 150c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.331
Gentex | GCC24-CR (Cont Horn, Mech, 15c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.115
Gentex | GCC24-CR (Cont Horn, Mech, 30c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.131
Gentex | GCC24-CR (Cont Horn, Mech, 75c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.219
Gentex | GCC24-CR (Cont Horn, Mech, 95c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.243
Gentex | GCC24-CR (Cont Horn, Mech, 115c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.257
Gentex | GCC24-CR (Cont Horn, Mech, 150c) | HN/SB 24V 15-115CD CEIL R | 0 | 0.329
Gentex | GCS24-CR (15c) | STRB 24V 15-110CD CEIL R | 0 | 0.072
Gentex | GCS24-CR (30c) | STRB 24V 15-110CD CEIL R | 0 | 0.088
Gentex | GCS24-CR (75c) | STRB 24V 15-110CD CEIL R | 0 | 0.176
Gentex | GCS24-CR (95c) | STRB 24V 15-110CD CEIL R | 0 | 0.2
Gentex | GCS24-CR (115c) | STRB 24V 15-110CD CEIL R | 0 | 0.214
Gentex | GCS24-CR (150c) | STRB 24V 15-110CD CEIL R | 0 | 0.286
Gentex | ST24-15W (15c) | STR24V15C RED IN | 0 | 0.08
Gentex | ST24-15/75W (15/75c) | STR24V15/75C RED IN | 0 | 0.119
Gentex | ST24-30W (30c) | STR24V30C RED IN | 0 | 0.119
Gentex | ST24-60W (60c) | STR24V60C RED IN | 0 | 0.172
Gentex | ST24-75W (75c) | STR24V75C RED IN | 0 | 0.204
Gentex | ST24-110W (110c) | STR24V110C RED IN | 0 | 0.252
System Sensor | SP2R1224MC (15c) | SPKRSTRB 2W 12/24V VCD RD | 0 | 0.064
System Sensor | SP2R1224MC (15/75c) | SPKRSTRB 2W 12/24V VCD RD | 0 | 0.074
System Sensor | SP2R1224MC (30c) | SPKRSTRB 2W 12/24V VCD RD | 0 | 0.093
System Sensor | SP2R1224MC (75c) | SPKRSTRB 2W 12/24V VCD RD | 0 | 0.158
System Sensor | SP2R1224MC (110c) | SPKRSTRB 2W 12/24V VCD RD | 0 | 0.208
System Sensor | SC2415 (15c) | STR CEIL RND 24V 15C RED | 0 | 0.068
System Sensor | SC241575 (15/75c) | STR CEIL RND 24V 1575C RD | 0 | 0.077
System Sensor | SC2430 (30c) | STR CEIL RND 24V 30C RED | 0 | 0.107
System Sensor | SC2475 (75c) | STROBE CIEL ROUND 24V RED | 0 | 0.197
System Sensor | SC2495 (95c) | STR CEIL RND 24V 95C RED | 0 | 0.239
System Sensor | SC24115 (115c) | STR CEIL RND 24V 115C RED | 0 | 0.298
System Sensor | SC24177 (177c) | STROBE 177CD 24V RED | 0 | 0.399
System Sensor | S1224MCK (15c) | STRB 12/24V WPROOF RED | 0 | 0.064
System Sensor | S1224MCK (15/75c) | STRB 12/24V WPROOF RED | 0 | 0.074
System Sensor | S1224MCK (30c) | STRB 12/24V WPROOF RED | 0 | 0.093
System Sensor | S1224MCK (75c) | STRB 12/24V WPROOF RED | 0 | 0.158
System Sensor | S1224MCK (110c) | STRB 12/24V WPROOF RED | 0 | 0.208
System Sensor | S1224MC (15c) | STROBE 12/24V VARC RED | 0 | 0.064
System Sensor | S1224MC (15/75c) | STROBE 12/24V VARC RED | 0 | 0.074
System Sensor | S1224MC (30c) | STROBE 12/24V VARC RED | 0 | 0.093
System Sensor | S1224MC (75c) | STROBE 12/24V VARC RED | 0 | 0.158
System Sensor | S1224MC (110c) | STROBE 12/24V VARC RED | 0 | 0.208
System Sensor | PC2415 (Temp Horn, Mech, 15c) | HRN/STRB RND CEIL 24V RED 15c | 0 | 0.076
System Sensor | PC241575 (Temp Horn, Mech, 15/75c) | HRN/STRB RND CEIL 24V RED15/75c | 0 | 0.091
System Sensor | PC2430 (Temp Horn, Mech, 30c) | HRN/STRB RND CEIL 24V RED 30c | 0 | 0.128
System Sensor | PC2475 (Temp Horn, Mech, 75c) | HRN/STRB RND CEIL 24V RED 75c | 0 | 0.222
System Sensor | PC2495 (Temp Horn, Mech, 95c) | HRN/STRB RND CEIL 24V RED 95c | 0 | 0.271
System Sensor | PC24115 (Temp Horn, Mech, 115c) | HRN/STRB RND CEIL 24V RED 115c | 0 | 0.296
System Sensor | PC24177 (Temp Horn, Mech, 177c) | HRN/STRB RND CEIL 24V RED 177c | 0 | 0.501
System Sensor | PC2415 (Temp Horn, 3000Hz, 15c) | HRN/STRB RND CEIL 24V RED 15c | 0 | 0.078
System Sensor | PC241575 (Temp Horn, 3000Hz, 15/75c) | HRN/STRB RND CEIL 24V RED15/75c | 0 | 0.092
System Sensor | PC2430 (Temp Horn, 3000Hz, 30c) | HRN/STRB RND CEIL 24V RED 30c | 0 | 0.128
System Sensor | PC2475 (Temp Horn, 3000Hz, 75c) | HRN/STRB RND CEIL 24V RED 75c | 0 | 0.222
System Sensor | PC2495 (Temp Horn, 3000Hz, 95c) | HRN/STRB RND CEIL 24V RED 95c | 0 | 0.271
System Sensor | PC24115 (Temp Horn, 3000Hz, 115c) | HRN/STRB RND CEIL 24V RED 115c | 0 | 0.296
System Sensor | PC24177 (Temp Horn, 3000Hz, 177c) | HRN/STRB RND CEIL 24V RED 177c | 0 | 0.496
System Sensor | PC2415 (Cont Horn, Mech, 15c) | HRN/STRB RND CEIL 24V RED 15c | 0 | 0.081
System Sensor | PC241575 (Cont Horn, Mech, 15/75c) | HRN/STRB RND CEIL 24V RED15/75c | 0 | 0.096
System Sensor | PC2430 (Cont Horn, Mech, 30c) | HRN/STRB RND CEIL 24V RED 30c | 0 | 0.131
System Sensor | PC2475 (Cont Horn, Mech, 75c) | HRN/STRB RND CEIL 24V RED 75c | 0 | 0.221
System Sensor | PC2495 (Cont Horn, Mech, 95c) | HRN/STRB RND CEIL 24V RED 95c | 0 | 0.269
System Sensor | PC24115 (Cont Horn, Mech, 115c) | HRN/STRB RND CEIL 24V RED 115c | 0 | 0.292
System Sensor | PC24177 (Cont Horn, Mech, 177c) | HRN/STRB RND CEIL 24V RED 177c | 0 | 0.491
System Sensor | PC2415 (Cont Horn, 3000Hz, 15c) | HRN/STRB RND CEIL 24V RED 15c | 0 | 0.086
System Sensor | PC241575 (Cont Horn, 3000Hz, 15/75c) | HRN/STRB RND CEIL 24V RED15/75c | 0 | 0.098
System Sensor | PC2430 (Cont Horn, 3000Hz, 30c) | HRN/STRB RND CEIL 24V RED 30c | 0 | 0.134
System Sensor | PC2475 (Cont Horn, 3000Hz, 75c) | HRN/STRB RND CEIL 24V RED 75c | 0 | 0.222
System Sensor | PC2495 (Cont Horn, 3000Hz, 95c) | HRN/STRB RND CEIL 24V RED 95c | 0 | 0.27
System Sensor | PC24115 (Cont Horn, 3000Hz, 115c) | HRN/STRB RND CEIL 24V RED 115c | 0 | 0.293
System Sensor | PC24177 (Cont Horn, 3000Hz, 177c) | HRN/STRB RND CEIL 24V RED 177c | 0 | 0.496
System Sensor | P1224MC (Temp Horn, Mech, 15c) | HRN STRB 12/24V VARC RED | 0 | 0.073
System Sensor | P1224MC (Temp Horn, Mech, 15/75c) | HRN STRB 12/24V VARC RED | 0 | 0.087
System Sensor | P1224MC (Temp Horn, Mech, 30c) | HRN STRB 12/24V VARC RED | 0 | 0.1
System Sensor | P1224MC (Temp Horn, Mech, 75c) | HRN STRB 12/24V VARC RED | 0 | 0.17
System Sensor | P1224MC (Temp Horn, Mech, 110c) | HRN STRB 12/24V VARC RED | 0 | 0.213
System Sensor | P1224MC (Cont Horn, 3000Hz, 15c) | HRN STRB 12/24V VARC RED | 0 | 0.075
System Sensor | P1224MC (Cont Horn, 3000Hz, 15/75c) | HRN STRB 12/24V VARC RED | 0 | 0.088
System Sensor | P1224MC (Cont Horn, 3000Hz, 30c) | HRN STRB 12/24V VARC RED | 0 | 0.1
System Sensor | P1224MC (Cont Horn, 3000Hz, 75c) | HRN STRB 12/24V VARC RED | 0 | 0.167
System Sensor | P1224MC (Cont Horn, 3000Hz, 110c) | HRN STRB 12/24V VARC RED | 0 | 0.21
System Sensor | SS-P2R(K) (Temp Horn, 15c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.088
System Sensor | SS-P2R(K) (Temp Horn, 15/75c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.097
System Sensor | SS-P2R(K) (Temp Horn, 30c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.112
System Sensor | SS-P2R(K) (Temp Horn, 75c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.168
System Sensor | SS-P2R(K) (Temp Horn, 95c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.19
System Sensor | SS-P2R(K) (Temp Horn, 110c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.21
System Sensor | SS-P2R(K) (Temp Horn, 115c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.218
System Sensor | SS-P2R(K) (Cont Horn, 15c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.103
System Sensor | SS-P2R(K) (Cont Horn, 15/75c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.112
System Sensor | SS-P2R(K) (Cont Horn, 30c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.126
System Sensor | SS-P2R(K) (Cont Horn, 75c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.181
System Sensor | SS-P2R(K) (Cont Horn, 95c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.203
System Sensor | SS-P2R(K) (Cont Horn, 110c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.221
System Sensor | SS-P2R(K) (Cont Horn, 115c) | HRN STRB 12/24V VARC WALL RED | 0 | 0.229
System Sensor | SS-P2W (Temp Horn, 15c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.088
System Sensor | SS-P2W (Temp Horn, 15/75c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.097
System Sensor | SS-P2W (Temp Horn, 30c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.112
System Sensor | SS-P2W (Temp Horn, 75c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.168
System Sensor | SS-P2W (Temp Horn, 95c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.19
System Sensor | SS-P2W (Temp Horn, 110c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.21
System Sensor | SS-P2W (Temp Horn, 115c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.218
System Sensor | SS-P2W (Cont Horn, 15c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.103
System Sensor | SS-P2W (Cont Horn, 15/75c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.112
System Sensor | SS-P2W (Cont Horn, 30c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.126
System Sensor | SS-P2W (Cont Horn, 75c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.181
System Sensor | SS-P2W (Cont Horn, 95c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.203
System Sensor | SS-P2W (Cont Horn, 110c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.221
System Sensor | SS-P2W (Cont Horn, 115c) | HRN STRB 12/24V VARC WALL WHT | 0 | 0.229
System Sensor | SS-PC2 (Temp Horn, 15c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.088
System Sensor | SS-PC2 (Temp Horn, 15/75c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.097
System Sensor | SS-PC2 (Temp Horn, 30c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.112
System Sensor | SS-PC2 (Temp Horn, 75c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.168
System Sensor | SS-PC2 (Temp Horn, 95c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.19
System Sensor | SS-PC2 (Temp Horn, 110c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.21
System Sensor | SS-PC2 (Temp Horn, 115c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.218
System Sensor | SS-PC2xH (Temp Horn, 135c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.215
System Sensor | SS-PC2xH (Temp Horn, 150c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.231
System Sensor | SS-PC2xH (Temp Horn, 177c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.258
System Sensor | SS-PC2xH (Temp Horn, 185c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.265
System Sensor | SS-PC2 (Cont Horn, 15c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.103
System Sensor | SS-PC2 (Cont Horn, 15/75c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.112
System Sensor | SS-PC2 (Cont Horn, 30c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.126
System Sensor | SS-PC2 (Cont Horn, 75c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.181
System Sensor | SS-PC2 (Cont Horn, 95c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.203
System Sensor | SS-PC2 (Cont Horn, 110c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.221
System Sensor | SS-PC2 (Cont Horn, 115c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.229
System Sensor | SS-PC2xH (Cont Horn, 135c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.233
System Sensor | SS-PC2xH (Cont Horn, 150c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.248
System Sensor | SS-PC2xH (Cont Horn, 177c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.275
System Sensor | SS-PC2xH (Cont Horn, 185c) | HRN STRB 12/24V VARC CEIL R/W | 0 | 0.281
System Sensor | SS-SRK (15c) | STRB 12/24V WPROOF WALL RED | 0 | 0.071
System Sensor | SS-SRK (15/75c) | STRB 12/24V WPROOF WALL RED | 0 | 0.081
System Sensor | SS-SRK (30c) | STRB 12/24V WPROOF WALL RED | 0 | 0.096
System Sensor | SS-SRK (75c) | STRB 12/24V WPROOF WALL RED | 0 | 0.153
System Sensor | SS-SRK (95c) | STRB 12/24V WPROOF WALL RED | 0 | 0.176
System Sensor | SS-SRK (110c) | STRB 12/24V WPROOF WALL RED | 0 | 0.195
System Sensor | SS-SRK (115c) | STRB 12/24V WPROOF WALL RED | 0 | 0.205
Users Choice | NAC Device 1 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 2 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 3 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 4 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 5 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 6 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 7 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 8 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 9 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 10 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 11 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 12 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 13 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 14 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 15 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 16 (Free to modify) | - | 0 | 0
Users Choice | NAC Device 17 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 1 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 2 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 3 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 4 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 5 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 6 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 7 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 8 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 9 (Free to modify) | - | 0 | 0
Users Choice for Aux Power | Aux Power Device 10 (Free to modify) | - | 0 | 0
OPTION BUS | D7030X, Eight Point LED Annuniciator |  | 0.035 | 0.035
OPTION BUS | D7031, Remote Reset Module |  | 0 | 0
OPTION BUS | D7032, Eight Point LED Annunciator Expander |  | 0.001 | 0.001
OPTION BUS | D7035 Octal Relay Module, Relays Power |  | 0.008 | 0.008
OPTION BUS | D7035 Octal Relay Module, Relays Power (Energized in Normal) |  | 0.008 | 0.008
OPTION BUS | D7048 Octal Driver Module |  | 0.01 | 0.01
OPTION BUS | FMR-1000-RA, Remote Annunciator |  | 0.02 | 0.15
OPTION BUS | FMR-1000-RCMD, Remote Command Center |  | 0.02 | 0.15
OPTION BUS | FPP-RNAC-8A-4C, Remote NAC Power Supply |  | 0.02 | 0.02
SLC | FAP-325-V2F, Photo Detector(flat head) | Input | 0.0004 | 0.0004
SLC | FAP-325-V2R, Photo Detector(round head) | Input | 0.0004 | 0.0004
SLC | FAP-325, Photo Detector | Input | 0.00039 | 0.00039
SLC | FAH-325, Heat Detector | Input | 0.00035 | 0.00035
SLC | FAI-325, Ionization Detector | Input | 0.00035 | 0.00035
SLC | FAH-440, Thermal Detector | Input | 0.00023 | 0.00023
SLC | FAP-440, Smoke Detector | Input | 0.00023 | 0.00023
SLC | FAP-440-D, Dual Smoke Detector | Input | 0.00023 | 0.00023
SLC | FAD-440-DH, Duct Detector | Input | 0.00023 | 0.00023
SLC | FAP-440-T, Multi-sensor (Smoke + Optical) | Input | 0.00023 | 0.00023
SLC | FAP-440-DT, Multi-sensor (Dual Smoke + Optical) | Input | 0.00023 | 0.00023
SLC | FAP-440-TC, Multi-sensor (Smoke + Optical + CO) | Input | 0.00023 | 0.00023
SLC | FAP-440-DTC, Multi-sensor (Dual Smoke + Optical + CO) | Input | 0.00023 | 0.00023
SLC | FAA-440-B4-ISO, FAA-440-B6-ISO(from SLC) | Input | 8e-05 | 8e-05
SLC | FLM-325-ISO(Short Circuit Isolator) | Input | 0.00027 | 0.00027
SLC | FAA-325-B6S, Aux Powered Sounder Base | Output | 0.00011 | 0.00011
SLC | FAD-325, Duct Detector (without relay) | INPUT | 0.00039 | 0.00039
SLC | FAD-325-R, Duct Detector (with relay) | INPUT | 0.00039 | 0.00039
SLC | FLM-325-CZM4, Conventional Zone Module | INPUT | 0.0004 | 0.0004
SLC | FLM-325-I4, Single Input Contact Module Class B (box with LED) | INPUT | 0.00055 | 0.00066
SLC | FLM-325-I4-A, Single Input Contact Module Class A(Used for FMM-325A/-D, without SCI) | INPUT | 0.00035 | 0.00066
SLC | FLM-325-I4-AI, Single Input Contact Module Class A(Used for FMM-325A/-D, with SCI) | INPUT | 0.00035 | 0.00066
SLC | FMM-325A/-D Analog Manual Station used with D339A, Contact Monitor Module | INPUT | 0.00055 | 0.00066
SLC | FMM-325A/-D Analog Manual Station used with FLM-325-IM, Miniature Contact Monitor Module | INPUT | 0.00034 | 0.00036
SLC | FLM-325-2I4, Dual Input Contact Module | INPUT | 0.0006 | 0.00072
SLC | D328A, Relay Module and FLM-325-ISO | Output | 0.00015 | 0.00015
SLC | FLM-325-2R4, Dual Relay Module(1 Amp Relay) | Output | 0.00015 | 0.00015
SLC | FLM-325-2R4-2A, Dual Relay Module(2 Amp Relay) | Output | 0.00015 | 0.00015
SLC | FLM-325-2R4-2AI, Dual Relay Module(2 Amp Relay, with SCI) | Output | 0.00015 | 0.00015
SLC | FLM-325-2R4-8A, Dual Relay Module(8Amp Relay) | Output | 0.00015 | 0.00015
SLC | FLM-325-2R4-8AI, Dual Relay Module(8Amp Relay, with SCI) | Output | 0.00015 | 0.00015
SLC | FLM-325-N4, NAC / Control Module Class B | Output | 0.00022 | 0.0003
SLC | FLM-325-NA4, NAC / Control Module Class A | Output | 0.00022 | 0.00022
SLC | FLM-325-NAI4, NAC / Control Module Class A with Isolator | Output | 0.00022 | 0.00042
CITY TIE | Local Energy Mode |  | 0.05 | 0.25
CITY TIE | Reverse Polarity |  | 0.005 | 0.033
NETWORK CARD | FPE-1000-NE (Network Card 2-Ethernet) |  | 0.1 | 0.1
NETWORK CARD | FPE-1000-NF (Network Card 1-Ethernet 2-Fiber) |  | 0.17 | 0.17
NETWORK CARD | FPE-1000-NW (Network Card 1-Ethernet 2-Wired) |  | 0.33 | 0.33
Note on E636: User can modify the colored part freely to add support for custom devices.
Print Device List

## Theoretical data (hidden)
Wait time for stability | 5s | Not related with device's number
ADC time | 200ms | With 1s interval
One shot polling | 60ms | When configure ASB's zone and pattern, one shot polling will be called with 1s interval
Reset wait time | 1.3s | When there are SOM serial or R2M serial, after SRI, 1.3s wait time is need.
Device type |  | Detector |  |  | Input device | [5 empty] | Output device | 440S
Steps\Device | Timing(ms) | Duct Heat | ALG-V | ALK-V | FRCME | FRCMA-Series | DIMM CZM | RM | R2M-L/LI SOM-A/AI | SOM R2M | ASB | 440S
Poll head type | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Poll status(Called in fullscan) | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Read type | 60 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Read sub type | 130 | 0 | 2 | 1 | 2 | 1 | 0 | 0 | 1 | 2 | 0 | 1
Write threshold | 230 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reset by addrress | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0
Configure zone | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Configure zone pattern | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Configure drill pattern | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
Poll rotary address | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Set working mode | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
One device init time | t | 350 | 610 | 480 | 380 | 250 | 120 | 440 | 570 | 700 | 1030 | 395
127 Devices initialization time | timing(s) | 60.5625 | 101.8375 | 81.2 | 65.325 | 44.6875 | 24.05 | 76.15 | 96.7875 | 117.425 | 181.7703 | 67.7062
254 Devices initialization time | timing(s) | 116.125 | 198.675 | 157.4 | 125.65 | 84.375 | 43.1 | 146 | 187.275 | 228.55 | 358.5405 | 130.4125
Device type |  | Line diameter limit (Accepts AWG line width) | Standby current (uA) | Alarm current (uA) |  | Timing (s) | Description | Max Address
Hochiki-CTN | Bosch-CTN
ALG-V | FAP-325, Photo Detector | 18 | 390 | 540 |  | 0.94226 | Input | 127
ALK-V | FAP-325-V2F, Photo Detector(flat head) | 18 | 390 | 800 |  | 0.6089 | Input | 254
ALK-V2 | FAP-325-V2R, Photo Detector(round head) | 18 | 390 | 800 |  | 0.6089 | Input | 254
ATG-EA | FAH-325, Heat Detector | 18 | 350 | 500 |  | 0.6089 | Input | 127
ASB | FAA-325-B6S, Aux Powered Sounder Base | 18 | 110 | 110 |  | 1.5171 | Output | 127
ISO | FLM-325-ISO(Short Circuit Isolator) | 18 | 270 | 270 |  | 0 | Input | 254
FRCME-4 | FLM-325-I4, Single Input Contact Module Class B (box with LED) | 14 | 550 | 660 |  | 0.53018 | INPUT | 127
FRCME-M | FMM-325A/-D Analog Manual Station used with FLM-325-IM, Miniature Contact Monitor Module | 14 | 339 | 358 |  | 0.53018 | INPUT | 254
FRCMA | FLM-325-I4-A, Single Input Contact Module Class A(Used for FMM-325A/-D, without SCI) | 14 | 630 | 820 |  | 0.53018 | INPUT | 254
FRCMA-I | FLM-325-I4-AI, Single Input Contact Module Class A(Used for FMM-325A/-D, with SCI) | 14 | 630 | 820 |  | 0.53018 | INPUT | 254
CZM | FLM-325-CZM4, Conventional Zone Module | 18 | 670 | 670 |  | 0.2021 | INPUT | 32
DIMM | FLM-325-2I4, Dual Input Contact Module | 14 | 600 | 720 |  | 0.2021 | INPUT | 127
R2M | FLM-325-2R4, Dual Relay Module(1 Amp Relay) | 18 | 390 | 400 |  | 0.93701 | Output | 127
R2M-L | FLM-325-2R4-2A, Dual Relay Module(2 Amp Relay) | 18 | 350 | 405 |  | 0.93701 | Output | 254
R2M-LI | FLM-325-2R4-2AI, Dual Relay Module(2 Amp Relay, with SCI) | 18 | 350 | 405 |  | 0.93701 | Output | 254
R2M-H | FLM-325-2R4-8A, Dual Relay Module(8Amp Relay) | 18 | 350 | 405 |  | 0.93701 | Output | 254
R2M-HI | FLM-325-2R4-8AI, Dual Relay Module(8Amp Relay, with SCI) | 18 | 350 | 405 |  | 0.93701 | Output | 254
SOM | FLM-325-N4, NAC / Control Module Class B | 18 | 154 | 161 |  | 0.93701 | Output | 64
SOM-A | FLM-325-NA4, NAC / Control Module Class A | 18 | 220 | 815.2 |  | 0.93701 | Output | 20
SOM-AI | FLM-325-NAI4, NAC / Control Module Class A with Isolator | 18 | 420 | 815.2 |  | 0.93701 | Output | 20
DH-98-A | FAD-325, Duct Detector (without relay) | 18 | 390 | 540 |  | 0.20735 | INPUT | 127
DH-98-AR | FAD-325-R, Duct Detector (with relay) | 18 | 390 | 540 |  | 0.20735 | INPUT | 127
RM | D328A, Relay Module and FLM-325-ISO | 18 | 150 | 150 |  | 0 | Output | 127
AIE-EA | FAI-325, Ionization Detector | 18 | 350 | 460 |  | 0.20735 | Input | 127
FRCME-4 | FMM-325A/-D Analog Manual Station used with D339A, Contact Monitor Module | 14 | 550 | 660 |  | 0.53018 | INPUT | 127
| FAP-440, Smoke Detector | 18 | 230 | 230 |  | 0.56693 | INPUT | 254
| FAP-440-DTC, Multi-sensor (Dual Smoke + Optical + CO) | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAH-440, Thermal Detector | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAP-440-D, Dual Smoke Detector | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAD-440-DH, Duct Detector | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAP-440-T, Multi-sensor (Smoke + Optical) | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAP-440-DT, Multi-sensor (Dual Smoke + Optical) | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAP-440-TC, Multi-sensor (Smoke + Optical + CO) | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
| FAA-440-B4-ISO, FAA-440-B6-ISO(from SLC) | 18 | 230 | 230 |  | 0.59722 | INPUT | 254
Wire AWG & Type | Ohms Per 1000 Ft.
12 | 2.01
14 | 3.19
16 | 4.03
18 | 6.41
R ---Resistance of the Line: (Line type, length) -- Ω
I ---Max current consumption on the devices: (Device type, number) -- mA
V --- Voltage on the measured A point (Rated 1.96V, should be less than 1.6V) -- V
Resistance Range | Factor V = A0*I+B0 | A0 | B0
R<=13 | No limit | 0 | 0
13<R<=16 | 0.01019 *I+ 0.0275 | 0.01019 | 0.0275
16<R<=19 | 0.01184 *I+ 0.0533 | 0.01184 | 0.0533
19<R<=22 | 0.01364 *I+ 0.0559 | 0.01364 | 0.0559
22<R<=25 | 0.01539 *I+ 0.0646 | 0.01539 | 0.0646

## Experiment data (hidden)
Setup: Link to emulator (TE-TLE), do re-plus test. |  |  | Test Result: restore time (s) |  |  |  | Average per device (s) | Time ratio
SLC1 | SLC2 | FMR | Round 1 | Round 2 | Round 3 | average
127 R2M | 127 R2M | 0
127 R2M | 64 R2M | 0
127 R2M | 0 | 0 | 118 | 120 | 119 | 119 | 0.93701 | 1
127 R2M | 0 | 1 | 118 | 119 | 118 | 118.3333 |  | 0.9944
127 R2M | 0 | 2 | 118 | 119 | 120 | 119 |  | 1
127 R2M | 0 | 3 | 120 | 118 | 119 | 119 |  | 1
127 R2M | 0 | 4 | 120 | 118 | 120 | 119.3333 |  | 1.0028
127 R2M | 0 | 5 | 120 | 119 | 118 | 119 |  | 1
127 R2M | 0 | 6 | 120 | 119 | 119 | 119.3333 |  | 1.0028
127 R2M | 0 | 7 | 119 | 120 | 119 | 119.3333 |  | 1.0028
127 R2M | 0 | 8 | 120 | 120 | 120 | 120 |  | 1.0084
127 ASB | 0 | 0 | 193 | 194 | 191 | 192.6667 | 1.5171 | 1
127 ASB | 0 | 1 | 191 | 194 | 201 | 195.3333 |  | 1.0138
127 ASB | 0 | 2 | 206 | 190 | 196 | 197.3333 |  | 1.0242
127 ASB | 0 | 3 | 191 | 198 | 195 | 194.6667 |  | 1.0104
127 ASB | 0 | 4 | 192 | 193 | 214 | 199.6667 |  | 1.0363
127 ASB | 0 | 5 | 207 | 212 | 191 | 203.3333 |  | 1.0554
127 ASB | 0 | 6 | 197 | 205 | 188 | 196.6667 |  | 1.0208
127 ASB | 0 | 7 | 196 | 195 | 191 | 194 |  | 1.0069
127 ASB | 0 | 8 | 193 | 211 | 204 | 202.6667 |  | 1.0519
127 ALG-V | 0 | 0 | 137 | 137 | 145 | 119.6667 | 0.94226 | 1
127 ALG-V | 0 | 1 | 139 | 140 | 148 | 122.3333 |  | 1.0223
127 ALG-V | 0 | 2 | 141 | 139 | 143 | 121 |  | 1.0111
127 ALG-V | 0 | 3 | 141 | 141 | 137 | 119.6667 |  | 1
127 ALG-V | 0 | 4 | 140 | 139 | 137 | 118.6667 |  | 0.99164
127 ALG-V | 0 | 5 | 144 | 144 | 143 | 123.6667 |  | 1.0334
127 ALG-V | 0 | 6 | 143 | 141 | 136 | 120 |  | 1.0028
127 ALG-V | 0 | 7 | 141 | 139 | 141 | 120.3333 |  | 1.0056
127 ALG-V | 0 | 8 | 137 | 141 | 137 | 118.3333 |  | 0.98886
127 DIMM | 0 | 0 | 26 | 25 | 26 | 25.6667 | 0.2021 | 1
127 DIMM | 0 | 1 | 25 | 25 | 27 | 25.6667 |  | 1
127 DIMM | 0 | 2 | 26 | 27 | 25 | 26 |  | 1.013
127 DIMM | 0 | 3 | 26 | 25 | 25 | 25.3333 |  | 0.98701
127 DIMM | 0 | 4 | 26 | 26 | 25 | 25.6667 |  | 1
127 DIMM | 0 | 5 | 25 | 25 | 26 | 25.3333 |  | 0.98701
127 DIMM | 0 | 6 | 25 | 25 | 26 | 25.3333 |  | 0.98701
127 DIMM | 0 | 7 | 26 | 25 | 25 | 25.3333 |  | 0.98701
127 DIMM | 0 | 8 | 25 | 25 | 25 | 25 |  | 0.97403
127 FRCME | 0 | 0 | 67 | 68 | 67 | 67.3333 | 0.53018 | 1
127 FRCME | 0 | 1 | 67 | 67 | 67 | 67 |  | 0.99505
127 FRCME | 0 | 2 | 68 | 67 | 66 | 67 |  | 0.99505
127 FRCME | 0 | 3 | 66 | 69 | 68 | 67.6667 |  | 1.005
127 FRCME | 0 | 4 | 68 | 68 | 69 | 68.3333 |  | 1.0149
127 FRCME | 0 | 5 | 67 | 66 | 67 | 66.6667 |  | 0.9901
127 FRCME | 0 | 6 | 69 | 68 | 67 | 68 |  | 1.0099
127 FRCME | 0 | 7 | 67 | 69 | 67 | 67.6667 |  | 1.005
127 FRCME | 0 | 8 | 68 | 67 | 66 | 67 |  | 0.99505
127 ALK-V | 0 | 0 |  |  |  | 0 | 0.6089 | 0
127 ALK-V | 0 | 1 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 2 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 3 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 4 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 5 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 6 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 7 |  |  |  | 0 |  | 0
127 ALK-V | 0 | 8 |  |  |  | 0 |  | 0
127 DH-98-A | 0 | 0 | 28 | 25 | 26 | 26.3333 | 0.20735 | 1
127 DH-98-A | 0 | 1 | 26 | 28 | 26 | 26.6667 |  | 1.0127
127 DH-98-A | 0 | 2 | 29 | 26 | 27 | 27.3333 |  | 1.038
127 DH-98-A | 0 | 3 | 26 | 25 | 27 | 26 |  | 0.98734
127 DH-98-A | 0 | 4 | 25 | 27 | 28 | 26.6667 |  | 1.0127
127 DH-98-A | 0 | 5 | 25 | 25 | 26 | 25.3333 |  | 0.96203
127 DH-98-A | 0 | 6 | 26 | 27 | 26 | 26.3333 |  | 1
127 DH-98-A | 0 | 7 | 28 | 26 | 27 | 27 |  | 1.0253
127 DH-98-A | 0 | 8 | 26 | 26 | 26 | 26 |  | 0.98734
FAP-440 | 0 | 0 | 144 | 144 | 144 | 144 | 0.56693 | 1
FAP-440 | 0 | 1 | 145 | 144 | 144 | 144.3333 |  | 1.0023
FAP-440 | 0 | 2 | 144 | 144 | 144 | 144 |  | 1
FAP-440 | 0 | 3 | 144 | 143 | 144 | 143.6667 |  | 0.99769
FAP-440 | 0 | 4 | 143 | 144 | 146 | 144.3333 |  | 1.0023
FAP-440 | 0 | 5 | 143 | 142 | 143 | 142.6667 |  | 0.99074
FAP-440 | 0 | 6 | 144 | 143 | 144 | 143.6667 |  | 0.99769
FAP-440 | 0 | 7 | 147 | 144 | 144 | 145 |  | 1.0069
FAP-440 | 0 | 8 | 147 | 145 | 144 | 145.3333 |  | 1.0093
FAP-440-DTC | 0 | 0 | 57 | 58 | 57 | 57.3333 | 0.59722 | 1
FAP-440-DTC | 0 | 1 | 58 | 59 | 59 | 58.6667 |  | 1.0233
FAP-440-DTC | 0 | 2 | 58 | 59 | 58 | 58.3333 |  | 1.0174
FAP-440-DTC | 0 | 3 | 58 | 59 | 60 | 59 |  | 1.0291
FAP-440-DTC | 0 | 4 | 58 | 57 | 61 | 58.6667 |  | 1.0233
FAP-440-DTC | 0 | 5 | 60 | 58 | 58 | 58.6667 |  | 1.0233
FAP-440-DTC | 0 | 6 | 57 | 58 | 60 | 58.3333 |  | 1.0174
FAP-440-DTC | 0 | 7 | 58 | 59 | 57 | 58 |  | 1.0116
FAP-440-DTC | 0 | 8 | 57 | 58 | 58 | 57.6667 |  | 1.0058