5.1 Transmission Components

The transmitter to receiver communication session is composed of three basic elements: the Handshake Tone sequence, Message Blocks, and Acknowledgements. The Handshake Tone sequence consists of a pair of single-frequency tones sequenced in time. The Message Blocks consist of a series of DTMF tone bursts separated by spaces. The Acknowledgement Tone is a single tone burst.

5.1.1 Handshake Tones

The Handshake Tone sequence is produced by the RECEIVER. The purpose is to signal the TRANSMITTER that the communication channel is ready.

5.1.1.1 Placement

5.1.1.2 Composition

A 1400 Hz / 800 ms or 1000 ms is also considered valid.

5.1.2 Message Blocks

A Message Block is sent by the TRANSMITTER for each message in the transmitter’s message queue. Each message block contains sufficient information to report an event in the system.

5.1.2.1 Placement

The first message block is sent beginning 250 msec. (250 min.,300 max.) after the end of either the Handshake Tone sequence or after a Kissoff (Acknowledgement) tone. The delay is timed from the end of the tone.

5.1.2.2 Message Composition

The form of the message is:

ACCT MT QXYZ GG CCC

where: ACCT = 4 Digit Account number (0-9, B-F)

MT = Message Type. This 2-digit sequence is used to identify the Contact ID message to the receiver. It may be transmitted as either 18 (preferred) or 98 (optional). New receiver implementations shall accept either a 18 or a 98. Note that some older recei

v

ers may not accept 98 .

Note 1:

With message type 58, the alarm string is as follows:

AAAA MT AAAAAA Q XYZ GG CCC P

68: Contact ID with ADT Capture.

Q = Event qualifier, which gives specific event information: 1 = New Event or Opening 3 = New Restore or Closing

6 = Previously reported condition still present (Status report)

XYZ = Event code (3 Hex digits 0-9,B-F)

GG = Group or Partition number (2 Hex digits 0-9, B-F). Use 00 to indicate that no specific group or partition information

applies. CCC = Zone number (Event reports) or User # (Open / Close reports ) (3 Hex digits 0-9,B-F ). Use 000 to indicate that no

specific zone or user information applies

S = 1 Digit Hex checksum calculated such that:

(Sum of all message digits + S) MOD 15 = 0

Note: A ‘0’ shall be transmitted as a 10 and valued as a 10 for checksum purposes even though it is displayed and printed as

‘0’. It uses the same tone pair as the ‘0’ (OPER) key on a standard telephone.

5.1.2.3 Data Tones

The details of the tones are contained in the following table.

Data Transmission Frequencies

Standard DTMF Signaling

| Digit | Low Tone (Hz.) |  | High Tone (Hz. ) |  | Digit Value |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0 | 941 |  | 1336 |  | 10 |  |  |
| 1 |  | 697 |  | 1209 |  |  | 1 |
| 2 |  | 697 |  | 1336 |  |  | 2 |
| 3 |  | 697 |  | 1477 |  |  | 3 |
| 4 |  | 770 |  | 1209 |  |  | 4 |

| 5 | 770 |  | 1336 |  | 5 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6 | 770 |  | 1477 |  | 6 |  |  |
| 7 |  | 852 |  | 1209 |  |  | 7 |
| 8 |  | 852 |  | 1336 |  |  | 8 |
| 9 |  | 852 |  | 1477 |  |  | 9 |
| B (*) |  | 941 |  | 1209 |  |  | 11 |
| C (#) |  | 941 |  | 1477 |  |  | 12 |
| D |  | 697 |  | 1633 |  |  | 13 |
| E |  | 770 |  | 1633 |  |  | 14 |
| F |  | 852 |  | 1633 |  |  | 15 |

Notes:

1) The digit ‘0’ is transmitted with a value of 10 and shall be counted as a 10 in the calculation of the message checksum.

2) The DTMF pair of 941 Hz. And 1633 Hz. is not used in this format and shall not be sent.

3) The frequency deviation on each of the above frequencies shall be ± 1.5% max.

5.1.3 Inter-Message Time

After sending its message, the transmitter should wait for 1.25 sec. for the start of a Kissoff Tone from the receiver. If the start of a kissoff tone is detected, the transmitter must continue timing the tone, even if the inter-message time expires. The panel must detect a minimum of 400 msec. of the Kissoff Tone for it to be considered to be valid.

If a Kissoff tone is detected, the transmitter should wait for the tone to end and then wait 250 msec. (250 min.,300 max.) before beginning the next message. If no Kissoff Tone is received, the transmitter should repeat the message after the expiration of the 1.25 second inter-message interval.

5.1.4 Kissoff (Acknowledgement) Tone

Note: Transmitters shall accept a frequency error of at least ± 5% to ensure back-compatibility with older receivers

5.1.5 Maximum Number Of Attempts

5.2    Data Codes

The data codes used to transmit events are contained in Appendix C: Event Codes.

Account 1234 is reporting a Perimeter Burglary Alarm on Zone 15 of Partition 1

1234 18 1131 01 015 8

5.3.2 Example 2 – Restoral Message

Account 1234 is reporting a Restore of a Perimeter Burglary Alarm on Zone 15 of Partition 1 The message shall be sent as:

1234 18 3131 01 015 6

where:

1234 = The account number (1234) 18 = The message type used to identify the message as Contact ID 3131 = The Event Qualifier (3) for a restoral, followed by the Event Code for Perimeter Burglary (131) 01 = The partition number (1) 015 = The zone number (015) 6 = The checksum (See Example 1)

5.3.3 Example 3 – Opening Message

User 3 disarms Partition 2 of Account 1234 The message shall be sent as:

1234 18 1401 02 003 5

where

1234 = The account number (1234) 18 = The message type used to identify the message as Contact ID 1401 = The Event Qualifier (1) for an Opening, followed by the Event Code for Open/Close by User (401)

02 = The partition number (2) 003 = The User number (003) 5 = The checksum (See Example

1)

5.3.4 Example 4 – Closing Message

User 5 arms Partition 3 of Account 1234

The message shall be sent as:

1234 18 3401 03 005 F

where

1234 = The account number    (1234) 18 = The message type used to identify the message as Contact ID 3401 = The Event Qualifier (3) for a Closing, followed by the Event Code for Open/Close by User (401) 03 = The partition number (2) 005 = The User number (003) F = The checksum (See Example 1)

Note the use of ‘F’ since the sum of the message digits is an even multiple of 15.

5.4 Message Transmission Flowchart

5.5 Event Codes

| Medical | Fire |  | System |  |  | Open/Close |  | System |  | Test |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fire |  |  | Sounder/Relay |  |  | Remote Access |  | Sounder/Rly |  | Log |  |
| Panic |  |  |  | Sys. Per. | Access Control |  | Sys. Per. |  | Sched. |  |  |
| Burglary |  |  |  | Comm. |  |  | Comm. |  |  |  |  |
| General |  |  | Prot. Loop |  |  |  |  |  |  |  |  |
| 24 Hour |  |  | Sensor |  |  |  |  |  |  |  |  |

The following table defines the Event Codes used in this protocol. The Data Type identifies the information sent in the CCC field as either Zone number or User number. The value in the CCC field should be set to 000 if no useful information is being sent.    Descriptions for the Event Codes will be added in a later revision of this standard.

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| ALARMS |  |  |
| Medical Alarms –100 |  |  |
| 100 Medical | Zone | A non-specific medical condition exists |
| 101 Personal Emergency | Zone | Emergency Assistance request |
| 102 Fail to report in | Zone | A user has failed to activate a monitoring device |
| Fire Alarms –110 |  |  |
| 110 Fire | Zone | A non-specific fire alarm condition exists |
| 111 Smoke | Zone | An alarm has been triggered by a smoke detector |
| 112 Combustion | Zone | An alarm has been triggered by a combustion detector |
| 113 Water flow | Zone | An alarm has been triggered by a water flow detector |
| 114 Heat | Zone | An alarm has been triggered by a heat detector |
| 115 Pull Station | Zone | A pull station has been activated |
| 116 Duct | Zone | An alarm has been triggered by a duct detector |
| 117 Flame | Zone | An alarm has been triggered by a flame detector |
| 118 Near Alarm | Zone | A near-alarm condition has been detected on a fire sensor |
| Panic Alarms –120 |  |  |
| 120 Panic | Zone | A non-specific hold-up alarm exists |
| 121 Duress | User | A duress code has been entered by a user |
| 122 Silent | Zone | A silent hold-up alarm exists |
| 123 Audible | Zone | An audible hold-up alarm exists |
| 124 Duress – Access granted | Zone | A duress code has been granted at an exit door |
| 125 Duress – Egress granted | Zone | A duress code has been entered at an entry door |
| 126 Hold-up suspicion print | User | A user has activated a trigger to indicate a suspicious condition |
| Burglar Alarms –130 |  |  |
| 130 Burglary | Zone | A burglary zone has been violated while armed |
| 131 Perimeter | Zone | A perimeter zone has been violated while armed |
| 132 Interior | Zone | An interior zone has been violated while armed |
| 133 24 Hour (Safe) | Zone | A 24 hour burglary zone has been violated |
| 134 Entry/Exit | Zone | An Entry/Exit zone has been violated while armed |
| 135 Day/night | Zone | A Day/Night zone has been violated while armed |
| 136 Outdoor | Zone | An outdoor burglary zone has been violated while armed |
| 137 Tamper | Zone | A burglary zone has been tampered with while armed |
| 138 Near alarm | Zone |  |
| 139 Intrusion Verifier | Zone |  |
| General Alarm – 140 |  |  |
|  | Zone |  |
| 140 General Alarm | Zone |  |
| 141 Polling loop open | Zone |  |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| 142 Polling loop short | Zone |  |
| 143 Expansion module failure | Zone |  |
| 144 Sensor tamper | Zone |  |
| 145 Expansion module tamper | Zone |  |
| 146 Silent Burglary | Zone |  |
| 147 Sensor Supervision Failure | Zone | A sensor has not reported in during an armed state |
| 24 Hour Non-Burglary - 150 and 160 |  |  |
| 150 24 Hour Non-Burglary | Zone |  |
| 151 Gas detected | Zone |  |
| 152 Refrigeration | Zone |  |
| 153 Loss of heat | Zone |  |
| 154 Water Leakage | Zone |  |
| 155 Foil Break | Zone |  |
| 156 Day Trouble | Zone |  |
| 157 Low bottled gas level | Zone |  |
| 158 High temp | Zone |  |
| 159 Low temp | Zone |  |
| 161 Loss of air flow | Zone |  |
| 162 Carbon Monoxide detected | Zone |  |
| 163 Tank level | Zone |  |
| SUPERVISORY |  |  |
| Fire Supervisory -200 and 210 |  |  |
| 200 Fire Supervisory | Zone |  |
| 201 Low water pressure | Zone |  |
| 202 Low CO2 | Zone |  |
| 203 Gate valve sensor | Zone |  |
| 204 Low water level | Zone |  |
| 205 Pump activated | Zone |  |
| 206 Pump failure | Zone |  |
| TROUBLES |  |  |
| System Troubles -300 and 310 |  |  |
| 300 System Trouble | Zone |  |
| 301 AC Loss | Zone |  |
| 302 Low system battery | Zone |  |
| 303 RAM Checksum bad | Zone |  |
| 304 ROM checksum bad | Zone |  |
| 305 System reset | Zone |  |
| 306 Panel programming changed | Zone |  |
| 307 Self-test failure | Zone |  |
| 308 System shutdown | Zone |  |
| 309 Battery test failure | Zone |  |
| 310 Ground fault | Zone |  |
| 311 Battery Missing/Dead | Zone |  |
| 312 Power Supply Overcurrent | Zone |  |
| 313 Engineer Reset | User |  |
| 314 Primary Power Supply Failure | Zone | The primary power supply has failed |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| Sounder / Relay Troubles -320 |  |  |
| 320 Sounder/Relay | Zone |  |
| 321 Bell 1 | Zone |  |
| 322 Bell 2 | Zone |  |
| 323 Alarm relay | Zone |  |
| 324 Trouble relay | Zone |  |
| 325 Reversing relay | Zone |  |
| 326 Notification Appliance Ckt. # 3 | Zone |  |
| 327 Notification Appliance Ckt. #4 | Zone |  |
| System Peripheral Trouble -330 and 340 |  |  |
| 330 System Peripheral trouble | Zone |  |
| 331 Polling loop open | Zone |  |
| 332 Polling loop short | Zone |  |
| 333 Expansion module failure | Zone |  |
| 334 Repeater failure | Zone |  |
| 335 Local printer out of paper | Zone |  |
| 336 Local printer failure | Zone |  |
| 337 Exp. Module DC Loss | Zone |  |
| 338 Exp. Module Low Batt. | Zone |  |
| 339 Exp. Module Reset | Zone |  |
| 341 Exp. Module Tamper | Zone |  |
| 342 Exp. Module AC Loss | Zone |  |
| 343 Exp. Module self-test fail | Zone |  |
| 344 RF Receiver Jam Detect | Zone | An RF receiver has detected continuous carrier |
| Communication Troubles -350 and 360 |  |  |
| 350 Communication trouble | Zone |  |
| 351 Telco 1 fault | Zone |  |
| 352 Telco 2 fault | Zone |  |
| 353 Long Range Radio xmitter fault | Zone |  |
| 354 Failure to communicate event | Zone |  |
| 355 Loss of Radio supervision | Zone |  |
| 356 Loss of central polling | Zone |  |
| 357 Long Range Radio VSWR problem | Zone |  |
| Protection Loop -370 |  |  |
| 370 Protection loop | Zone |  |
| 371 Protection loop open | Zone |  |
| 372 Protection loop short | Zone |  |
| 373 Fire trouble | Zone |  |
| 374 Exit error alarm (zone) | Zone |  |
| 375 Panic zone trouble | Zone |  |
| 376 Hold-up zone trouble | Zone |  |
| 377 Swinger Trouble | Zone | A zone that has previously exceeded the max. alarm report count for swingers has faulted again (SIA False Alarm) |
| 378 Cross-zone Trouble | Zone | Only one of the sensors in a cross-zoned pair has triggered within a 5 minute window (SIA False Alarm) |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| Sensor Trouble -380 |  |  |
| 380 Sensor trouble | Zone |  |
| 381 Loss of supervision -RF | Zone |  |
| 382 Loss of supervision -RPM | Zone |  |
| 383 Sensor tamper | Zone |  |
| 384 RF low battery | Zone |  |
| 385 Smoke detector Hi sensitivity | Zone |  |
| 386 Smoke detector Low sensitivity | Zone |  |
| 387 Intrusion detector Hi sensitivity | Zone |  |
| 388 Intrusion detector Low sensitivity | Zone |  |
| 389 Sensor self-test failure | Zone |  |
| 391 Sensor Watch trouble | Zone |  |
| 392 Drift Compensation Error | Zone |  |
| 393 Maintenance Alert | Zone |  |
| OPEN/CLOSE/REMOTE ACCESS |  |  |
| Open/Close -400, 440,450,460 |  |  |
| 400 Open/Close | User |  |
| 401 O/C by user | User |  |
| 402 Group O/C | User |  |
| 403 Automatic O/C | User |  |
| 404 Late to O/C (Note: use 453, 454 instead ) | User |  |
| 405 Deferred O/C (Obsolete- do not use ) | User |  |
| 406 Cancel | User |  |
| 407 Remote arm/disarm | User |  |
| 408 Quick arm | User |  |
| 409 Keyswitch O/C | User |  |
| 441 Armed STAY | User |  |
| 442 Keyswitch Armed STAY | User |  |
| 450 Exception O/C | User |  |
| 451 Early O/C | User |  |
| 452 Late O/C | User |  |
| 453 Failed to Open | User |  |
| 454 Failed to Close | User |  |
| 455 Auto-arm Failed | User |  |
| 456 Partial Arm | User |  |
| 457 Exit Error (user) | User |  |
| 458 User on Premises | User |  |
| 459 Recent Close | User |  |
| 461 Wrong Code Entry | Zone |  |
| 462 Legal Code Entry | User |  |
| 463 Re-arm after Alarm | User |  |
| 464 Auto-arm Time Extended | User |  |
| 465 Panic Alarm Reset | Zone |  |
| 466 Service On/Off Premises | User | An alarm service person has entered / left the premises |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| Remote Access –410 |  |  |
| 411 Callback request made | User |  |
| 412 Successful download/access | User |  |
| 413 Unsuccessful access | User |  |
| 414 System shutdown command received | User |  |
| 415 Dialer shutdown command received | User |  |
| 416 Successful Upload | Zone |  |
| Access control –420,430 |  |  |
| 421 Access denied | User |  |
| 422 Access report by user | User |  |
| 423 Forced Access | Zone |  |
| 424 Egress Denied | User |  |
| 425 Egress Granted | User |  |
| 426 Access Door propped open | Zone |  |
| 427 Access point Door Status Monitor trouble | Zone |  |
| 428 Access point Request To Exit trouble | Zone |  |
| 429 Access program mode entry | User |  |
| 430 Access program mode exit | User |  |
| 431 Access threat level change | User |  |
| 432 Access relay/trigger fail | Zone |  |
| 433 Access RTE shunt | Zone |  |
| 434 Access DSM shunt | Zone |  |
| 435 Second Person Access | User | The second person required for a 2 person operation has entered a code |
| 436 Irregular Access | User | An access out of the normal time window has occurred |
| BYPASSES / DISABLES |  |  |
| System Disables -500 and 510 |  |  |
| 501 Access reader disable | Zone |  |
| Sounder / Relay Disables –520 |  |  |
| 520 Sounder/Relay Disable | Zone |  |
| 521 Bell 1 disable | Zone |  |
| 522 Bell 2 disable | Zone |  |
| 523 Alarm relay disable | Zone |  |
| 524 Trouble relay disable | Zone |  |
| 525 Reversing relay disable | Zone |  |
| 526 Notification Appliance Ckt. # 3 disable | Zone |  |
| 527 Notification Appliance Ckt. # 4 disable | Zone |  |
| System Peripheral Disables -530 and 540 |  |  |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| 531 Module Added | Zone |  |
| 532 Module Removed | Zone |  |
| Communication Disables -550 and 560 |  |  |
| 551 Dialer disabled | Zone |  |
| 552 Radio transmitter disabled | Zone |  |
| 553 Remote Upload/Download disabled | Zone |  |
| Bypasses –570 |  |  |
| 570 Zone/Sensor bypass | Zone |  |
| 571 Fire bypass | Zone |  |
| 572 24 Hour zone bypass | Zone |  |
| 573 Burg. Bypass | Zone |  |
| 574 Group bypass | User |  |
| 575 Swinger bypass | Zone |  |
| 576 Access zone shunt | Zone |  |
| 577 Access point bypass | Zone |  |
| 578 Vault Bypass | Zone | A vault protection zone has been bypassed |
| 579 Vent Zone Bypass | Zone | A vent zone (window) has been bypassed so it can be left open |
| TEST / MISC. |  |  |
| Test/Misc. –600, 610 |  |  |
| 601 Manual trigger test report | Zone |  |
| 602 Periodic test report | Zone |  |
| 603 Periodic RF transmission | Zone |  |
| 604 Fire test | User |  |
| 605 Status report to follow | Zone |  |
| 606 Listen-in to follow | Zone |  |
| 607 Walk test mode | User |  |
| 608 Periodic test - System Trouble Present | Zone |  |
| 609 Video Xmitter active | Zone |  |
| 611 Point tested OK | Zone |  |
| 612 Point not tested | Zone |  |
| 613 Intrusion Zone Walk Tested | Zone |  |
| 614 Fire Zone Walk Tested | Zone |  |
| 615 Panic Zone Walk Tested | Zone |  |
| 616 Service Request | Zone |  |
| Event Log –620 |  |  |
| 621 Event Log reset | Zone |  |
| 622 Event Log 50% full | Zone |  |
| 623 Event Log 90% full | Zone |  |
| 624 Event Log overflow | Zone |  |
| 625 Time/Date reset | User |  |
| 626 Time/Date inaccurate | Zone |  |

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| 627 Program mode entry | Zone |  |
| 628 Program mode exit | Zone |  |
| 629 32 Hour Event log marker | Zone |  |
| Scheduling –630 |  |  |
| 630 Schedule change | Zone |  |
| 631 Exception schedule change | Zone |  |
| 632 Access schedule change | Zone |  |
| Personnel Monitoring -640 |  |  |
| 641 Senior Watch Trouble | Zone |  |
| 642 Latch-key Supervision | User |  |
| Misc. –650, 700 |  |  |
| 651 Reserved for Ademco Use | Zone |  |
| 652 Reserved for Ademco Use | User |  |
| 653 Reserved for Ademco Use | User |  |
| 654 System Inactivity | Zone | The system has not been armed for a preset number of days |
| 703 Auxiliary #3 | Zone | Old Westgarde code –unknown meaning |
| 704 Installer Test | Zone | Old Westgarde code – unknown meaning |
| 750-789 “User Assigned” |  | * See note below |
| 796 Unable to output signal (Derived Channel) | Zone |  |
| 798 STU Controller down (Derived Channel) | Zone |  |
| 900 Download Abort | Zone | A downloading process was aborted manually |
| 901 Download Start/End | Zone | A download session started/ended |
| 902 Download Interrupted | Zone | A downloading session was interrupted |
| 910 Auto-close with Bypass | Zone | A system auto-armed itself and bypassed one or more zones in the process |
| 911 Bypass Closing | Zone | A system was armed with one or more zones bypassed |
| 912 Fire Alarm Silence | Zone | A fire alarm has been silenced |
| 913 Supervisory Point test Start/End | User | A serviceman test of supervisory-type zones has started /ended |
| 914 Hold-up test Start/End | User | A serviceman test of hold-up-type zones has started /ended |
| 915 Burg. Test Print Start/End | User | (Local only – no dialer) |
| 916 Supervisory Test Print Start/End | User | (Local only – no dialer) |
| 917 Burg. Diagnostics Start/End | Zone |  |
| 918 Fire Diagnostics Start/End | Zone |  |
| 919 Untyped diagnostics | Zone |  |
| 920 Trouble Closing (closed with burg. during exit) | User | The system was armed but a burg alarm occurred during the exit delay period |
| 921 Access Denied Code Unknown | User | Logs refusal to grant access |

Note – “User Defined” Event codes

Event codes in the 750-789 range hve been reserved for “User Assigned”    reports. These event codes may be used for nonstandard events that do not fit within industry definitions. Since the definition of these codes may vary from company to company, and even from account to account, it is the Central Station’s responsibility to manage their code assignments.

| Event | Data Type | Descriptions (to be supplied in a later revision of this standard) |
| --- | --- | --- |
| 922 Supervisory Point Alarm | Zone |  |
| 923 Supervisory Point Bypass | Zone |  |
| 924 Supervisory Point Trouble | Zone |  |
| 925 Hold-up Point Bypass | Zone |  |
| 926 AC Failure for 4 hours | Zone |  |
| 927 Output Trouble | Zone |  |
| 928 User code for event | User | Provides user info to indicate which user bypassed a point |
| 929 Log-off | User |  |